## Summary
Physical Properties of 3MTM NovecTM 1230 Fire Protection Fluid
Property | Unit | Value | Data Source
Molecular Weight |  | 316.05
Boiling Point | °C | 49.2 | from vapor pressure measurements
Freezing Point | °C | -108 | measured value
Critical Temperature | °C | 168.66 | measured value
Critical Pressure | kPa | 1865 | measured value
Critical Volume | cc/mole | 494.5 | Vc=ZcRTc /Pc
Critical Density | kg/m3 | 639.1 | calculated from Vc
Specific Heat, Liquid @ 25°C | kJ/kg°C | 1.103 | measured value
Specific Heat, vapor @ constant P (1atm & 25°C) | kJ/kg°C | 0.891 | measured value
Heat of vaporization @ bp | kJ/kg | 88 | measured value
Thermal Conductivity of liquid @ 25°C | W/m°C | 0.0588 | measured value
Viscosity, liquid @ 25°C | cp | 0.524 | measured value
Relative Dielectric Strength @ 1 atm (N2=1.0) | - | 2.3 | measured value
Solubility of water in agent @ 21°C | wt% | <0.001 | based upon detection limits
Vapor Pressure @ 25°C | kPa | 40.36 | measured value

## Symbols and Units
Symbols and Units used in Tables and Diagram
Property | Symbol | Units
Temperature | T | °C or K
Pressure | P | bar or psi
Volume | V | m3/kg
Compressibility | Z | -
Enthalpy | H | kJ/kg
Entropy | S | kJ/kg K
Specific Heat | CP, CP | kJ/kg K
Heat Capacity Ratio | CP/CV,CP/CV | -
Speed of Sound | CS | m/s
Density | r | g/cm3 or kg/m3
Viscosity | n | centistokes
Surface Tension | s | dynes/cm
Thermal Conductivity | l | mW/m K
Liquid Mole Fraction | x | -
Vapor Mole Fraction | y | -

## PRSV Equation of State
PRSV Equation of State for 3MTM NovecTM 1230 Fire Protection Fluid
The experimental properties measured for 3M Novec 1230 fluid were used to develop a thermodynamic model using the PRSV (Peng-Robinson-Stryjek-Vera) equation of state:
P = RT/(V - b) - aa/[V(V + b) + b(V - b)]
where a = 0.457235(RTc)2/Pc
b = 0.077796RTc/Pc
a = ko + k1(1 + Tr0.5)(0.7 – Tr)
ko = 0.378893 + 1.4897153w – 0.17131848w2 + 0.0196554w3
Tr = T/Tc
Constants used in the PRSV Equation of State for 3M Novec 1230 fluid
Molecular Weight | 316.046
Tc, K | 441.81
Pc, bars | 18.646
Zc | 0.251
Acentric Factor, w | 0.471
k1 | 0.052
Note: The critical temperature, pressure and compressibility factor of 3MTM NovecTM 1230 fluid are measured values. The acentric factor was determined from the measured critical properties and from the vapor pressure measurements reported below. The value of kappa shown above gives the best overall fit of the measured vapor pressure using the PRSV equation of state.
The PRSV equation predicts liquid densities that are about 3% higher than the corresponding experimental values. Therefore, a volume shift has been incorporated into the model. The volume shift is applied after completing the thermodynamic calculations. Therefore, only the liquid density and volume values reported in the tables are affected. The volume shift was also applied in obtaining the constant volume lines on the P-H diagram. The compressibility factors shown in the tables are the values obtained from the PRSV equation without the volume shift. This shift was not applied to the vapor.
The volume shift was incorporated as follows:
V = VPRSV – VSHIFT
Where V is tha actual molar volume, VPRSV is the molar volume calculated via the PRSV equation of state and VSHIFT is the molar volume correction, all in m3/mol. The molar volume correction was determined from a 4th order polynomial expression:
VSHIFT = A = Br* + C(r*)2 + D(r*)3 + E(r*)4
where r* = 1/(VPRSV) – 1/(VC)
Volume Shift Parameters used for Liquid Volumes and Densities:
|  | A | -8.025e-05
|  | B | 5.8563e-08
|  | C | -6.7539e-12
|  | D | -2.0126e-15
|  | E | 3.3304e-19

## Vapor Pressure
Vapor Pressure Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
T(°C) | Pmeas (psia) | Pcorr (psia) | % Dev.(a) | PPRSV (psia) | % Dev.(b)
0.01 | 1.831 | 1.828 | -0.17 | 1.826 | -0.27
5 | 2.353 | 2.355 | 0.1 | 2.353 | 0.01
10 | 2.995 | 3.003 | 0.26 | 3 | 0.18
15 | 3.791 | 3.79 | -0.04 | 3.787 | -0.1
20 | 4.728 | 4.735 | 0.15 | 4.733 | 0.11
25 | 5.853 | 5.862 | 0.16 | 5.862 | 0.16
30 | 7.179 | 7.194 | 0.22 | 7.198 | 0.26
35 | 8.736 | 8.758 | 0.26 | 8.768 | 0.36
40 | 10.636 | 10.579 | -0.54 | 10.583 | -0.49
44.99 | 12.768 | 12.684 | -0.66 | 12.68 | -0.69
50 | 15.241 | 15.108 | -0.87 | 15.097 | -0.95
55 | 18.003 | 17.877 | -0.7 | 17.863 | -0.78
50 | 15.126 | 15.107 | -0.12 | 15.097 | -0.19
60.61 | 21.246 | 21.436 | 0.89 | 21.424 | 0.83
70.56 | 28.787 | 29.059 | 0.94 | 29.076 | 1
79.83 | 37.691 | 37.893 | 0.54 | 37.985 | 0.78
89.88 | 49.451 | 49.641 | 0.38 | 49.886 | 0.88
99.98 | 64.119 | 64.047 | -0.11 | 64.539 | 0.65
99.96 | 64.068 | 64.019 | -0.08 | 64.51 | 0.69
109.95 | 81.345 | 81.23 | -0.14 | 82.065 | 0.88
119.99 | 102.113 | 101.919 | -0.19 | 103.179 | 1.04
129.97 | 126.855 | 126.355 | -0.39 | 128.062 | 0.95
139.99 | 155.612 | 155.38 | -0.15 | 157.437 | 1.17
150.11 | 189.852 | 189.976 | 0.07 | 192.071 | 1.16
155 | 208.951 | 208.901 | -0.02 | 210.804 | 0.88
160.03 | 229.485 | 229.971 | 0.21 | 231.459 | 0.86
168.66(c) | 270.440(c) | 270.552 | 0.04 | zc = 0.251
Correlation:
with P in psia and T in Kelvin
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas
(b) % Dev. = 100 x (PPRSV - Pmeas)/Pmeas
(c) These are the values of the critical temperature, pressure and compressibility factor that were measured using a visual critical point apparatus.

## N2 Solubility
Nitrogen Solubility Measurements in 3MTM NovecTM 1230 Fire Protection Fluid
Henry's Law Constant
Temperature | Pressure | N2, Mole Fraction |  | P*x/y
° C | psia | Vapor | Liquid | psia
0 | 100.4 | 0.978 | 0.0298 | 3295.0067
0 | 250.1 | 0.9892 | 0.0737 | 3356.8374
0 | 500.2 | 0.9925 | 0.1437 | 3454.7564
0 | 750.2 | 0.9931 | 0.207 | 3599.1479
0 | 950.2 | 0.9931 | 0.2546 | 3706.3771
30 | 250.2 | 0.9607 | 0.0718 | 3347.7318
30 | 500.3 | 0.9748 | 0.1402 | 3478.5481
30 | 750.3 | 0.9786 | 0.202 | 3634.8692
60 | 100.6 | 0.7564 | 0.0225 | 3381.9484
60 | 250 | 0.8886 | 0.0686 | 3238.3382
60 | 500.1 | 0.932 | 0.141 | 3305.6255
60 | 750.1 | 0.9451 | 0.2083 | 3403.3582
60 | 950.2 | 0.9496 | 0.2579 | 3498.6813

## Vapor Density
Measured and Calculated Vapor Density of 3MTM NovecTM 1230 Fire Protection Fluid
Vapor Density (g/cm3)
Temperature (°C) | Pressure (psia) | Measured | PRSV(a) | % Dev.(b)
80.15 | 14.11 | 0.010814 | 0.010928 | 1.06
80.1 | 19.88 | 0.015719 | 0.015696 | -0.15
80.12 | 25.66 | 0.020846 | 0.020669 | -0.85
80.15 | 30.9 | 0.025712 | 0.025367 | -1.34
100.06 | 23.2 | 0.017373 | 0.017316 | -0.33
100.01 | 31.47 | 0.024421 | 0.024065 | -1.46
100.01 | 39.49 | 0.031455 | 0.030958 | -1.58
100.01 | 47.57 | 0.038937 | 0.038302 | -1.63
100 | 55.06 | 0.046367 | 0.045528 | -1.81
124.89 | 62.06 | 0.046649 | 0.047247 | 1.28
124.89 | 71.76 | 0.055648 | 0.056187 | 0.97
124.89 | 80.72 | 0.064539 | 0.064985 | 0.69
124.9 | 89.06 | 0.073368 | 0.073721 | 0.48
124.9 | 96.59 | 0.081884 | 0.082149 | 0.32
124.9 | 104.37 | 0.091403 | 0.091495 | 0.1
149.88 | 19.71 | 0.012582 | 0.012623 | 0.33
149.88 | 37.35 | 0.024752 | 0.024694 | -0.23
149.89 | 53.38 | 0.036485 | 0.0364 | -0.23
149.89 | 68.4 | 0.048139 | 0.048111 | -0.06
149.89 | 82.41 | 0.059717 | 0.059793 | 0.13
149.9 | 95.69 | 0.071471 | 0.071657 | 0.26
149.88 | 108.32 | 0.083381 | 0.0838 | 0.5
149.9 | 119.73 | 0.095129 | 0.095604 | 0.5
149.91 | 130.47 | 0.10695 | 0.1076 | 0.61
149.88 | 140.18 | 0.11856 | 0.11937 | 0.69
149.9 | 149.19 | 0.1302 | 0.13119 | 0.76
149.9 | 157.43 | 0.14183 | 0.14297 | 0.81
149.9 | 164.99 | 0.15364 | 0.15479 | 0.75
149.91 | 171.84 | 0.16546 | 0.16653 | 0.65
149.88 | 178.03 | 0.17731 | 0.17831 | 0.56
174.89 | 22.58 | 0.013582 | 0.013625 | 0.32
174.89 | 46.59 | 0.029142 | 0.029121 | -0.07
174.88 | 68.15 | 0.044077 | 0.044063 | -0.03
174.89 | 88.01 | 0.058719 | 0.058829 | 0.19
174.88 | 107.56 | 0.074164 | 0.074472 | 0.42
174.89 | 124.97 | 0.088971 | 0.089483 | 0.58
174.89 | 140.82 | 0.10344 | 0.1042 | 0.74
174.89 | 155.88 | 0.11816 | 0.11929 | 0.95
174.88 | 169.79 | 0.1329 | 0.13436 | 1.1
174.9 | 182.73 | 0.14768 | 0.14951 | 1.24
174.88 | 194.25 | 0.16196 | 0.16418 | 1.37
174.88 | 205.31 | 0.1768 | 0.17946 | 1.51
174.88 | 215.44 | 0.1917 | 0.19471 | 1.57
174.89 | 224.55 | 0.20635 | 0.20967 | 1.61
174.9 | 232.85 | 0.22118 | 0.22457 | 1.53
174.89 | 240.57 | 0.2358 | 0.23981 | 1.7
174.89 | 247.62 | 0.25077 | 0.25512 | 1.74
174.88 | 253.98 | 0.26571 | 0.27042 | 1.77
174.88 | 259.69 | 0.28057 | 0.28559 | 1.79
174.89 | 264.6 | 0.29478 | 0.29997 | 1.76
174.88 | 269.46 | 0.31038 | 0.31596 | 1.8
174.88 | 273.53 | 0.32516 | 0.33088 | 1.76
174.88 | 277.15 | 0.33981 | 0.34571 | 1.74
174.88 | 280.39 | 0.3548 | 0.36059 | 1.63
174.89 | 283.23 | 0.36943 | 0.37504 | 1.52
174.89 | 285.61 | 0.38436 | 0.3887 | 1.13
174.89 | 288 | 0.39889 | 0.40406 | 1.29
(a) Vapor density obtained from the PRSV equation of state without the volume shift.
(b) % Dev. = 100 x (PRSV-Meas)/Meas

## Liquid Density at 1 atm
Liquid Density Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Liquid Density, g/cm3
Temperature °C | Measured | Correlated | % Dev.(a)
30.9 | 1.5838 | 1.5847 | 0.055651
25.6 | 1.5998 | 1.6001 | 0.01704
20.8 | 1.6148 | 1.614 | -0.048811
1.2 | 1.672 | 1.6709 | -0.063983
-8.5 | 1.6994 | 1.6991 | -0.017712
-18.2 | 1.7263 | 1.7273 | 0.056062
-28 | 1.7527 | 1.7557 | 0.1727
-37.7 | 1.7718 | 1.7839 | 0.68268
Linear fit of measured density data
r = -0.002904 * T + 1.674415
r in g/cm3, T in°C
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas

## Saturated Liquid Density
Measured and Calculated Saturated Liquid Density of 3MTM NovecTM 1230 Fire Protection Fluid
Liquid Density (g/cm3)
Temperature (°C) | Pressure (psia) | Measured | PRSV(a) | % Dev.(b)
10 | 3.003 | 1.6451 | 1.6371 | -0.49
20 | 4.734 | 1.615 | 1.6079 | -0.44
30 | 7.194 | 1.5852 | 1.5776 | -0.48
40 | 10.579 | 1.5551 | 1.5462 | -0.57
10 | 3.003 | 1.645 | 1.6371 | -0.48
20 | 4.734 | 1.6142 | 1.6079 | -0.39
30 | 7.194 | 1.5845 | 1.5776 | -0.44
40 | 10.579 | 1.5543 | 1.5462 | -0.52
168.66(c) | 270.44(c) | 0.6392(c) | 0.6393 | 0.02
(a) Liquid density obtained from the PRSV equation of state with the volume shift.
(b) % Dev. = 100 x (PRSV-Meas)/Meas
(c) These are the values of the critical temperature, pressure and density factor that were measured using a visual critical point apparatus.

## Compressed Liquid Density
Measured and Calculated Compressed Liquid Density of 3MTM NovecTM 1230 Fire Protection Fluid
Liquid Density (g/cm3)
Temperature (°C) | Pressure (psia) | Measured | PRSV(a) | % Dev.(b)
6.98 | 972 | 1.6839 | 1.6837 | -0.01
6.98 | 788 | 1.6795 | 1.6772 | -0.14
6.98 | 526 | 1.6731 | 1.6674 | -0.34
6.98 | 277 | 1.6667 | 1.6574 | -0.56
23.95 | 1930 | 1.6654 | 1.677 | 0.69
23.95 | 1516 | 1.6556 | 1.6627 | 0.43
23.95 | 1020 | 1.6426 | 1.6437 | 0.07
23.95 | 762 | 1.6356 | 1.6329 | -0.17
23.95 | 512 | 1.6283 | 1.6216 | -0.41
23.95 | 267 | 1.621 | 1.6098 | -0.69
49.49 | 1892 | 1.6047 | 1.618 | 0.83
49.49 | 1524 | 1.5935 | 1.6021 | 0.54
49.49 | 1047 | 1.5773 | 1.5791 | 0.11
49.49 | 776 | 1.5676 | 1.5645 | -0.19
49.49 | 514 | 1.5575 | 1.5492 | -0.53
49.49 | 264 | 1.5471 | 1.5331 | -0.9
74.43 | 1882 | 1.5418 | 1.5589 | 1.11
74.43 | 1529 | 1.5281 | 1.5403 | 0.8
74.43 | 1036 | 1.5067 | 1.5107 | 0.26
74.43 | 764 | 1.4937 | 1.492 | -0.11
74.43 | 505 | 1.4801 | 1.4722 | -0.53
74.43 | 263 | 1.4661 | 1.4514 | -1
99.38 | 1625 | 1.4646 | 1.4824 | 1.22
99.38 | 1498 | 1.4582 | 1.4739 | 1.08
99.38 | 1037 | 1.432 | 1.4395 | 0.52
99.38 | 762 | 1.4143 | 1.4154 | 0.08
99.38 | 506 | 1.3953 | 1.3895 | -0.41
99.38 | 262 | 1.3742 | 1.3605 | -1
124.34 | 1303 | 1.3729 | 1.3908 | 1.3
124.34 | 1015 | 1.3498 | 1.3627 | 0.96
124.34 | 760 | 1.3263 | 1.3335 | 0.54
124.34 | 517 | 1.2994 | 1.2999 | 0.04
124.34 | 252 | 1.2618 | 1.2518 | -0.79
(a) Liquid density obtained from the PRSV equation of state with the volume shift.
(b) % Dev. = 100 x (PRSV-Meas)/Meas

## Liquid Surface Tension at 1 atm
Liquid Surface Tension Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Surface Tension, dyne/cm
Temperature °C | measured | correlated | % Dev.(a)
6.8 | 12.47 | 12.3921 | -0.62445
6.9 | 12.44 | 12.3847 | -0.44465
7 | 12.44 | 12.3772 | -0.5045
12.2 | 11.98 | 11.9899 | 0.082651
12.3 | 11.98 | 11.9824 | 0.020445
12.4 | 11.95 | 11.975 | 0.20918
12.5 | 11.95 | 11.9675 | 0.14681
16.6 | 11.69 | 11.6619 | -0.24058
16.7 | 11.66 | 11.6544 | -0.047875
16.8 | 11.69 | 11.647 | -0.36818
20.1 | 11.39 | 11.4008 | 0.094465
23.1 | 11.08 | 11.1768 | 0.87374
24.5 | 11.01 | 11.0723 | 0.56546
25 | 10.8 | 11.0349 | 2.1751
28.7 | 10.59 | 10.7584 | 1.5905
28.8 | 10.56 | 10.751 | 1.8083
31.3 | 10.81 | 10.564 | -2.2754
31.9 | 10.51 | 10.5191 | 0.087039
33.5 | 10.68 | 10.3994 | -2.6269
34 | 10.54 | 10.362 | -1.6885
34.8 | 10.22 | 10.3022 | 0.80397
34.9 | 10.22 | 10.2947 | 0.73073
s in dynes/cm, T in °C
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas

## Liquid Viscosity at 1 atm
Liquid Viscosity Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Kinematic Viscosity, centistokes
Temperature °C | measured | correlated | % Dev.(a)
-40 | 1.2815 | 1.2873 | 0.44982
-30 | 1.014 | 1.0099 | -0.40588
-20 | 0.8165 | 0.81393 | -0.31494
-10 | 0.6805 | 0.67106 | -1.387
0 | 0.5555 | 0.56405 | 1.54
10 | 0.4773 | 0.48202 | 0.98877
24.93 | 0.3922 | 0.39125 | -0.24269
29.74 | 0.3686 | 0.36793 | -0.1811
34.66 | 0.3473 | 0.34642 | -0.25283
38.62 | 0.3312 | 0.33062 | -0.17464
Correlation
n = exp(660.0991/(T + 200) - 3.8731)
n in centistokes, Temperature in °C
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas

## Dielectric Strength
Dielectric Strength Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Breakdown voltage (BDV) of Novec 1230 fluid vapor under saturated conditions at 1 atm, 21°C over a 2.7 mm electrode gap
Rate of | BDV | BDV |  | Average Value
Voltage Rise | dry N2 | Novec 1230 | Rel to N2 | Rel to N2
(volts/s) | (kV) | (kV)
3000 | 7.2 | 15.3 | 2.125
3000 | 6.7 | 15.8 | 2.3582
3000 | 7 | 15.2 | 2.1714
3000 | 7.1 | 16.4 | 2.3099
3000 | 6.8 | 16.2 | 2.3824 | 2.2694
2000 | 7 | 16 | 2.2857
2000 | 6.7 | 16 | 2.3881
2000 | 6.7 | 16 | 2.3881
2000 | 7.1 | 15.5 | 2.1831
2000 | 7.1 | 16 | 2.2535 | 2.2997
500 | 6.5 | 14.6 | 2.2462
500 | 6.4 | 14.4 | 2.25
500 | 6.4 | 15.2 | 2.375
500 | 6.8 | 15.8 | 2.3235
500 | 6.8 | 15.3 | 2.25 | 2.2889
BDV of liquid Novec 1230 fluid under these conditions is 48 kV.

## Vapor Heat Capacity
Calculated Vapor Heat Capacity (J/gK) of 3MTM NovecTM 1230 Fire Protection Fluid at Saturation Pressure
T(°C) | PRSV | Corr | % Deviation(a)
-10 | 0.8772 | 0.8774 | 0.02%
-8 | 0.8777 | 0.8778 | 0.02%
-6 | 0.8782 | 0.8783 | 0.01%
-4 | 0.8788 | 0.8788 | 0%
-2 | 0.8794 | 0.8794 | 0%
0 | 0.88 | 0.88 | 0%
2 | 0.8806 | 0.8806 | 0%
4 | 0.8813 | 0.8813 | 0%
6 | 0.882 | 0.882 | 0%
8 | 0.8828 | 0.8827 | -0.01%
10 | 0.8836 | 0.8835 | -0.01%
12 | 0.8844 | 0.8843 | -0.01%
14 | 0.8853 | 0.8852 | -0.01%
16 | 0.8862 | 0.8861 | -0.01%
18 | 0.8871 | 0.8871 | -0.01%
20 | 0.8881 | 0.888 | -0.01%
22 | 0.8891 | 0.8891 | -0.01%
24 | 0.8901 | 0.8901 | 0%
26 | 0.8912 | 0.8912 | 0%
28 | 0.8923 | 0.8923 | 0%
30 | 0.8935 | 0.8935 | 0%
32 | 0.8947 | 0.8947 | 0%
34 | 0.896 | 0.896 | 0%
36 | 0.8972 | 0.8973 | 0.01%
38 | 0.8984 | 0.8986 | 0.02%
40 | 0.8997 | 0.9 | 0.03%
42 | 0.9012 | 0.9014 | 0.02%
44 | 0.9026 | 0.9028 | 0.02%
46 | 0.9041 | 0.9043 | 0.02%
48 | 0.9056 | 0.9058 | 0.02%
50 | 0.9072 | 0.9074 | 0.02%
52 | 0.9089 | 0.909 | 0.01%
54 | 0.9106 | 0.9106 | 0%
56 | 0.9123 | 0.9123 | 0%
58 | 0.9141 | 0.914 | -0.01%
60 | 0.916 | 0.9158 | -0.03%
Quadratic Fit of Calculated Vapor Heat Capacity of L-15566:
with Cp in J/gK and T in Kelvin
(a) % Dev. = 100 x (Corr-PRSV)/PRSV

## Liquid Heat Capacity
Measured and Calculated Liquid Heat Capacity (J/gK) of 3MTM NovecTM 1230 Fire Protection Fluid at Saturation Pressure
T(°C) | Measured | PRSV | % Dev(a)
-10 | 1.0889 | 1.0872 | -0.16
-8 | 1.0894 | 1.088 | -0.13
-6 | 1.09 | 1.0888 | -0.11
-4 | 1.0906 | 1.0897 | -0.08
-2 | 1.0913 | 1.0906 | -0.06
0 | 1.0919 | 1.0916 | -0.03
2 | 1.0926 | 1.0926 | 0
4 | 1.0933 | 1.0936 | 0.02
6 | 1.0941 | 1.0947 | 0.05
8 | 1.0949 | 1.0959 | 0.09
10 | 1.0957 | 1.0971 | 0.13
12 | 1.0966 | 1.0984 | 0.17
14 | 1.0975 | 1.0997 | 0.2
16 | 1.0984 | 1.1011 | 0.25
18 | 1.0993 | 1.1025 | 0.29
20 | 1.1003 | 1.104 | 0.33
22 | 1.1013 | 1.1055 | 0.38
24 | 1.1024 | 1.1071 | 0.43
26 | 1.1035 | 1.1087 | 0.47
28 | 1.1046 | 1.1104 | 0.53
30 | 1.1057 | 1.1123 | 0.6
32 | 1.1069 | 1.114 | 0.64
34 | 1.1081 | 1.1159 | 0.7
36 | 1.1093 | 1.1179 | 0.77
38 | 1.1106 | 1.1015 | -0.82
40 | 1.1119 | 1.1037 | -0.74
42 | 1.1132 | 1.1059 | -0.66
44 | 1.1146 | 1.1082 | -0.57
46 | 1.116 | 1.1106 | -0.48
48 | 1.1174 | 1.1131 | -0.39
50 | 1.1189 | 1.1157 | -0.28
52 | 1.1204 | 1.1183 | -0.18
54 | 1.1219 | 1.1211 | -0.07
56 | 1.1234 | 1.1238 | 0.03
58 | 1.125 | 1.1268 | 0.16
60 | 1.1266 | 1.1299 | 0.29
Quadratic Fit of Measured Liquid Heat Capacity of L-15566:
with Cp in J/gK and T in Kelvin
(a) % Dev. = 100 x (PRSV-Meas)/Meas

## Liquid Thermal Conductivity
Liquid Thermal Conductivity Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Thermal Conductivity, mW/(m*K)
Temperature °C | measured | correlated | % Dev.(a)
0 | 63.39 | 63.403 | 0.020508
20 | 59.67 | 59.643 | -0.045249
35 | 56.81 | 56.823 | 0.022883
Correlation
l = - 0.188*T + 63.403
l in mW/(m*K), Temperature in °C
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas
measurements made at 1 atm

## Vapor Thermal Conductivity
Vapor Thermal Conductivity Measurements on 3MTM NovecTM 1230 Fire Protection Fluid
Thermal Conductivity, mW/(m*K)
Temperature °C | measured | correlated | % Dev.(a)
50 | 5.82 | 5.7867 | -0.57216
70 | 6.45 | 6.4987 | 0.75504
90 | 7.24 | 7.2107 | -0.4047
Correlation
l = 0.0356*T + 4.0067
l in mW/(m*K), Temperature in °C
(a) % Dev. = 100 x (Pcorr - Pmeas)/Pmeas
measurements made at 1 atm

## Saturated Properties
Thermodynamic Properties of the Saturated Liquid and Vapor Phases for 3MTM NovecTM 1230 Fire Protection Fluid
|  | Saturated Liquid Phase |  |  |  |  | Saturated Vapor Phase
T K | T °C | P bars | r kg/m3 | Z | H kJ/kg | S kJ/kgK | P bars | r kg/m3 | Z | H kJ/kg | S kJ/kgK | ΔHvap kJ/kg
233.15 | -40 | 0.01 | 1766 | 9e-05 | 0 | 0 | 0.01 | 0.1638 | 0.99861 | 109.342 | 0.4689 | 109.342
234.15 | -39 | 0.011 | 1763.69 | 0.0001 | 1.081 | 0.0046 | 0.011 | 0.176 | 0.99851 | 110.214 | 0.4707 | 109.133
235.15 | -38 | 0.012 | 1761.37 | 0.0001 | 2.163 | 0.0092 | 0.012 | 0.189 | 0.99842 | 111.086 | 0.4724 | 108.923
236.15 | -37 | 0.013 | 1759.04 | 0.00011 | 3.244 | 0.0138 | 0.013 | 0.2028 | 0.99831 | 111.958 | 0.4741 | 108.713
237.15 | -36 | 0.014 | 1756.7 | 0.00012 | 4.326 | 0.0184 | 0.014 | 0.2175 | 0.9982 | 112.829 | 0.4759 | 108.503
238.15 | -35 | 0.015 | 1754.35 | 0.00013 | 5.407 | 0.0229 | 0.015 | 0.233 | 0.99809 | 113.701 | 0.4776 | 108.293
239.15 | -34 | 0.016 | 1751.99 | 0.00014 | 6.489 | 0.0274 | 0.016 | 0.2495 | 0.99797 | 114.572 | 0.4794 | 108.083
240.15 | -33 | 0.017 | 1749.61 | 0.00015 | 7.571 | 0.032 | 0.017 | 0.2669 | 0.99784 | 115.443 | 0.4811 | 107.872
241.15 | -32 | 0.018 | 1747.23 | 0.00016 | 8.653 | 0.0365 | 0.018 | 0.2854 | 0.99771 | 116.314 | 0.4829 | 107.662
242.15 | -31 | 0.019 | 1744.83 | 0.00017 | 9.735 | 0.0409 | 0.019 | 0.3049 | 0.99757 | 117.185 | 0.4847 | 107.451
243.15 | -30 | 0.021 | 1742.43 | 0.00018 | 10.817 | 0.0454 | 0.021 | 0.3256 | 0.99743 | 118.056 | 0.4864 | 107.24
244.15 | -29 | 0.022 | 1740.01 | 0.00019 | 11.899 | 0.0498 | 0.022 | 0.3474 | 0.99727 | 118.927 | 0.4882 | 107.028
245.15 | -28 | 0.024 | 1737.58 | 0.00021 | 12.981 | 0.0543 | 0.024 | 0.3704 | 0.99711 | 119.798 | 0.49 | 106.817
246.15 | -27 | 0.025 | 1735.14 | 0.00022 | 14.064 | 0.0587 | 0.025 | 0.3947 | 0.99695 | 120.669 | 0.4918 | 106.605
247.15 | -26 | 0.027 | 1732.69 | 0.00024 | 15.147 | 0.0631 | 0.027 | 0.4203 | 0.99677 | 121.539 | 0.4935 | 106.393
248.15 | -25 | 0.029 | 1730.23 | 0.00025 | 16.23 | 0.0674 | 0.029 | 0.4473 | 0.99659 | 122.41 | 0.4953 | 106.18
249.15 | -24 | 0.031 | 1727.76 | 0.00027 | 17.313 | 0.0718 | 0.031 | 0.4757 | 0.9964 | 123.28 | 0.4971 | 105.967
250.15 | -23 | 0.033 | 1725.28 | 0.00028 | 18.396 | 0.0761 | 0.033 | 0.5057 | 0.9962 | 124.151 | 0.4989 | 105.754
251.15 | -22 | 0.035 | 1722.78 | 0.0003 | 19.48 | 0.0804 | 0.035 | 0.5372 | 0.99599 | 125.021 | 0.5007 | 105.541
252.15 | -21 | 0.038 | 1720.28 | 0.00032 | 20.564 | 0.0847 | 0.038 | 0.5703 | 0.99577 | 125.891 | 0.5025 | 105.327
253.15 | -20 | 0.04 | 1717.76 | 0.00034 | 21.648 | 0.089 | 0.04 | 0.6051 | 0.99554 | 126.761 | 0.5043 | 105.114
254.15 | -19 | 0.043 | 1715.24 | 0.00036 | 22.732 | 0.0933 | 0.043 | 0.6416 | 0.99531 | 127.631 | 0.5061 | 104.899
255.15 | -18 | 0.045 | 1712.7 | 0.00038 | 23.817 | 0.0976 | 0.045 | 0.68 | 0.99506 | 128.501 | 0.5079 | 104.685
256.15 | -17 | 0.048 | 1710.15 | 0.00041 | 24.902 | 0.1018 | 0.048 | 0.7202 | 0.9948 | 129.371 | 0.5097 | 104.47
257.15 | -16 | 0.051 | 1707.59 | 0.00043 | 25.987 | 0.106 | 0.051 | 0.7624 | 0.99454 | 130.241 | 0.5115 | 104.254
258.15 | -15 | 0.054 | 1705.02 | 0.00046 | 27.072 | 0.1103 | 0.054 | 0.8066 | 0.99426 | 131.111 | 0.5133 | 104.038
259.15 | -14 | 0.058 | 1702.44 | 0.00048 | 28.158 | 0.1145 | 0.058 | 0.853 | 0.99397 | 131.98 | 0.5151 | 103.822
260.15 | -13 | 0.061 | 1699.85 | 0.00051 | 29.244 | 0.1186 | 0.061 | 0.9015 | 0.99368 | 132.85 | 0.5169 | 103.605
261.15 | -12 | 0.065 | 1697.24 | 0.00054 | 30.331 | 0.1228 | 0.065 | 0.9523 | 0.99337 | 133.719 | 0.5187 | 103.388
262.15 | -11 | 0.069 | 1694.63 | 0.00057 | 31.418 | 0.127 | 0.069 | 1.0054 | 0.99304 | 134.588 | 0.5205 | 103.171
263.15 | -10 | 0.073 | 1692 | 0.0006 | 32.505 | 0.1311 | 0.073 | 1.0609 | 0.99271 | 135.458 | 0.5223 | 102.953
264.15 | -9 | 0.077 | 1689.36 | 0.00064 | 33.593 | 0.1352 | 0.077 | 1.1189 | 0.99236 | 136.327 | 0.5241 | 102.734
265.15 | -8 | 0.082 | 1686.71 | 0.00067 | 34.68 | 0.1393 | 0.082 | 1.1795 | 0.992 | 137.196 | 0.526 | 102.515
266.15 | -7 | 0.086 | 1684.05 | 0.00071 | 35.769 | 0.1434 | 0.086 | 1.2428 | 0.99163 | 138.064 | 0.5278 | 102.296
267.15 | -6 | 0.091 | 1681.38 | 0.00075 | 36.858 | 0.1475 | 0.091 | 1.3089 | 0.99125 | 138.933 | 0.5296 | 102.075
268.15 | -5 | 0.096 | 1678.7 | 0.00079 | 37.947 | 0.1516 | 0.096 | 1.3778 | 0.99085 | 139.802 | 0.5314 | 101.855
269.15 | -4 | 0.102 | 1676 | 0.00083 | 39.037 | 0.1556 | 0.102 | 1.4496 | 0.99044 | 140.67 | 0.5332 | 101.634
270.15 | -3 | 0.107 | 1673.3 | 0.00087 | 40.127 | 0.1597 | 0.107 | 1.5245 | 0.99001 | 141.539 | 0.5351 | 101.412
271.15 | -2 | 0.113 | 1670.58 | 0.00092 | 41.217 | 0.1637 | 0.113 | 1.6025 | 0.98957 | 142.407 | 0.5369 | 101.19
272.15 | -1 | 0.119 | 1667.85 | 0.00097 | 42.308 | 0.1677 | 0.119 | 1.6838 | 0.98912 | 143.275 | 0.5387 | 100.967
273.15 | 0 | 0.126 | 1665.12 | 0.00102 | 43.4 | 0.1717 | 0.126 | 1.7683 | 0.98865 | 144.143 | 0.5405 | 100.743
274.15 | 1 | 0.132 | 1662.36 | 0.00107 | 44.492 | 0.1757 | 0.132 | 1.8564 | 0.98816 | 145.011 | 0.5424 | 100.519
275.15 | 2 | 0.139 | 1659.6 | 0.00112 | 45.584 | 0.1797 | 0.139 | 1.9479 | 0.98766 | 145.878 | 0.5442 | 100.294
276.15 | 3 | 0.147 | 1656.83 | 0.00118 | 46.677 | 0.1836 | 0.147 | 2.0431 | 0.98715 | 146.746 | 0.546 | 100.068
277.15 | 4 | 0.154 | 1654.04 | 0.00124 | 47.771 | 0.1876 | 0.154 | 2.142 | 0.98662 | 147.613 | 0.5478 | 99.842
278.15 | 5 | 0.162 | 1651.25 | 0.0013 | 48.865 | 0.1915 | 0.162 | 2.2448 | 0.98607 | 148.48 | 0.5497 | 99.615
279.15 | 6 | 0.17 | 1648.44 | 0.00136 | 49.96 | 0.1955 | 0.17 | 2.3516 | 0.9855 | 149.347 | 0.5515 | 99.387
280.15 | 7 | 0.179 | 1645.62 | 0.00142 | 51.055 | 0.1994 | 0.179 | 2.4625 | 0.98492 | 150.214 | 0.5533 | 99.159
281.15 | 8 | 0.188 | 1642.79 | 0.00149 | 52.151 | 0.2033 | 0.188 | 2.5775 | 0.98432 | 151.081 | 0.5552 | 98.93
282.15 | 9 | 0.197 | 1639.95 | 0.00156 | 53.248 | 0.2072 | 0.197 | 2.6969 | 0.98371 | 151.947 | 0.557 | 98.7
283.15 | 10 | 0.207 | 1637.1 | 0.00164 | 54.345 | 0.2111 | 0.207 | 2.8207 | 0.98307 | 152.814 | 0.5588 | 98.469
284.15 | 11 | 0.217 | 1634.23 | 0.00171 | 55.443 | 0.2149 | 0.217 | 2.949 | 0.98242 | 153.68 | 0.5606 | 98.237
285.15 | 12 | 0.227 | 1631.35 | 0.00179 | 56.541 | 0.2188 | 0.227 | 3.0821 | 0.98175 | 154.545 | 0.5625 | 98.004
286.15 | 13 | 0.238 | 1628.47 | 0.00187 | 57.64 | 0.2226 | 0.238 | 3.2199 | 0.98106 | 155.411 | 0.5643 | 97.771
287.15 | 14 | 0.249 | 1625.57 | 0.00196 | 58.74 | 0.2265 | 0.249 | 3.3627 | 0.98035 | 156.277 | 0.5661 | 97.537
288.15 | 15 | 0.261 | 1622.66 | 0.00205 | 59.84 | 0.2303 | 0.261 | 3.5106 | 0.97962 | 157.142 | 0.568 | 97.302
289.15 | 16 | 0.273 | 1619.73 | 0.00214 | 60.941 | 0.2341 | 0.273 | 3.6636 | 0.97887 | 158.007 | 0.5698 | 97.066
290.15 | 17 | 0.285 | 1616.8 | 0.00223 | 62.043 | 0.2379 | 0.285 | 3.822 | 0.97811 | 158.872 | 0.5716 | 96.828
291.15 | 18 | 0.298 | 1613.85 | 0.00233 | 63.146 | 0.2417 | 0.298 | 3.9859 | 0.97732 | 159.736 | 0.5734 | 96.59
292.15 | 19 | 0.312 | 1610.89 | 0.00243 | 64.249 | 0.2455 | 0.312 | 4.1553 | 0.97651 | 160.6 | 0.5753 | 96.351
293.15 | 20 | 0.326 | 1607.92 | 0.00254 | 65.353 | 0.2492 | 0.326 | 4.3305 | 0.97568 | 161.464 | 0.5771 | 96.111
294.15 | 21 | 0.34 | 1604.94 | 0.00265 | 66.458 | 0.253 | 0.34 | 4.5116 | 0.97483 | 162.328 | 0.5789 | 95.87
295.15 | 22 | 0.355 | 1601.95 | 0.00276 | 67.563 | 0.2567 | 0.355 | 4.6988 | 0.97396 | 163.192 | 0.5807 | 95.628
296.15 | 23 | 0.371 | 1598.95 | 0.00287 | 68.67 | 0.2605 | 0.371 | 4.8921 | 0.97307 | 164.055 | 0.5826 | 95.385
297.15 | 24 | 0.387 | 1595.93 | 0.00299 | 69.777 | 0.2642 | 0.387 | 5.0918 | 0.97215 | 164.918 | 0.5844 | 95.141
298.15 | 25 | 0.404 | 1592.9 | 0.00312 | 70.885 | 0.2679 | 0.404 | 5.298 | 0.97122 | 165.78 | 0.5862 | 94.895
299.15 | 26 | 0.421 | 1589.86 | 0.00324 | 71.994 | 0.2716 | 0.421 | 5.5108 | 0.97026 | 166.643 | 0.588 | 94.649
300.15 | 27 | 0.439 | 1586.81 | 0.00338 | 73.103 | 0.2753 | 0.439 | 5.7304 | 0.96927 | 167.504 | 0.5899 | 94.401
301.15 | 28 | 0.457 | 1583.75 | 0.00351 | 74.214 | 0.279 | 0.457 | 5.957 | 0.96827 | 168.366 | 0.5917 | 94.152
302.15 | 29 | 0.476 | 1580.67 | 0.00365 | 75.325 | 0.2827 | 0.476 | 6.1908 | 0.96724 | 169.227 | 0.5935 | 93.902
303.15 | 30 | 0.496 | 1577.59 | 0.0038 | 76.438 | 0.2864 | 0.496 | 6.4318 | 0.96619 | 170.088 | 0.5953 | 93.651
304.15 | 31 | 0.516 | 1574.49 | 0.00395 | 77.551 | 0.29 | 0.516 | 6.6803 | 0.96511 | 170.949 | 0.5971 | 93.398
305.15 | 32 | 0.537 | 1571.37 | 0.0041 | 78.665 | 0.2937 | 0.537 | 6.9365 | 0.96401 | 171.809 | 0.5989 | 93.144
306.15 | 33 | 0.558 | 1568.25 | 0.00426 | 79.78 | 0.2973 | 0.558 | 7.2005 | 0.96289 | 172.669 | 0.6007 | 92.889
307.15 | 34 | 0.581 | 1565.12 | 0.00443 | 80.896 | 0.301 | 0.581 | 7.4724 | 0.96174 | 173.529 | 0.6026 | 92.632
308.15 | 35 | 0.604 | 1561.97 | 0.0046 | 82.014 | 0.3046 | 0.604 | 7.7526 | 0.96056 | 174.388 | 0.6044 | 92.374
309.15 | 36 | 0.627 | 1558.81 | 0.00477 | 83.132 | 0.3082 | 0.627 | 8.0411 | 0.95937 | 175.246 | 0.6062 | 92.115
310.15 | 37 | 0.652 | 1555.67 | 0.00495 | 85.132 | 0.3147 | 0.652 | 8.3354 | 0.95815 | 176.112 | 0.608 | 90.98
311.15 | 38 | 0.677 | 1552.52 | 0.00513 | 86.234 | 0.3182 | 0.677 | 8.6379 | 0.95691 | 176.97 | 0.6098 | 90.737
312.15 | 39 | 0.702 | 1549.36 | 0.00532 | 87.336 | 0.3218 | 0.702 | 8.9491 | 0.95565 | 177.828 | 0.6117 | 90.492
313.15 | 40 | 0.729 | 1546.18 | 0.00552 | 88.44 | 0.3253 | 0.729 | 9.2694 | 0.95436 | 178.686 | 0.6135 | 90.246
314.15 | 41 | 0.756 | 1543 | 0.00572 | 89.545 | 0.3288 | 0.756 | 9.5988 | 0.95305 | 179.543 | 0.6153 | 89.998
315.15 | 42 | 0.784 | 1539.8 | 0.00592 | 90.651 | 0.3323 | 0.784 | 9.9375 | 0.95171 | 180.399 | 0.6171 | 89.749
316.15 | 43 | 0.813 | 1536.59 | 0.00614 | 91.758 | 0.3358 | 0.813 | 10.2859 | 0.95034 | 181.256 | 0.6189 | 89.498
317.15 | 44 | 0.843 | 1533.36 | 0.00635 | 92.866 | 0.3393 | 0.843 | 10.644 | 0.94894 | 182.111 | 0.6207 | 89.245
318.15 | 45 | 0.873 | 1530.13 | 0.00658 | 93.976 | 0.3428 | 0.873 | 11.0121 | 0.94752 | 182.966 | 0.6225 | 88.991
319.15 | 46 | 0.905 | 1526.88 | 0.00681 | 95.086 | 0.3463 | 0.905 | 11.3905 | 0.94607 | 183.821 | 0.6243 | 88.735
320.15 | 47 | 0.937 | 1523.62 | 0.00705 | 96.198 | 0.3497 | 0.937 | 11.7793 | 0.9446 | 184.675 | 0.6261 | 88.477
321.15 | 48 | 0.97 | 1520.34 | 0.00729 | 97.311 | 0.3532 | 0.97 | 12.1787 | 0.94309 | 185.529 | 0.6279 | 88.218
322.15 | 49 | 1.005 | 1517.05 | 0.00754 | 98.426 | 0.3567 | 1.005 | 12.589 | 0.94156 | 186.382 | 0.6297 | 87.956
323.15 | 50 | 1.04 | 1513.76 | 0.0078 | 99.541 | 0.3601 | 1.04 | 13.0104 | 0.93999 | 187.234 | 0.6315 | 87.693
324.15 | 51 | 1.076 | 1510.44 | 0.00806 | 100.658 | 0.3636 | 1.076 | 13.4432 | 0.9384 | 188.086 | 0.6333 | 87.428
325.15 | 52 | 1.113 | 1507.12 | 0.00833 | 101.776 | 0.367 | 1.113 | 13.8877 | 0.93678 | 188.938 | 0.6351 | 87.161
326.15 | 53 | 1.151 | 1503.78 | 0.00861 | 102.896 | 0.3704 | 1.151 | 14.3439 | 0.93513 | 189.788 | 0.6368 | 86.892
327.15 | 54 | 1.19 | 1500.43 | 0.0089 | 104.017 | 0.3738 | 1.19 | 14.8123 | 0.93345 | 190.639 | 0.6386 | 86.622
328.15 | 55 | 1.23 | 1497.06 | 0.00919 | 105.139 | 0.3773 | 1.23 | 15.293 | 0.93174 | 191.488 | 0.6404 | 86.349
329.15 | 56 | 1.271 | 1493.68 | 0.00949 | 106.263 | 0.3807 | 1.271 | 15.7863 | 0.93 | 192.337 | 0.6422 | 86.074
330.15 | 57 | 1.314 | 1490.29 | 0.0098 | 107.388 | 0.3841 | 1.314 | 16.2926 | 0.92823 | 193.185 | 0.644 | 85.797
331.15 | 58 | 1.357 | 1486.89 | 0.01012 | 108.515 | 0.3875 | 1.357 | 16.812 | 0.92643 | 194.033 | 0.6457 | 85.518
332.15 | 59 | 1.401 | 1483.47 | 0.01045 | 109.643 | 0.3909 | 1.401 | 17.3448 | 0.9246 | 194.88 | 0.6475 | 85.237
333.15 | 60 | 1.447 | 1480.04 | 0.01078 | 110.772 | 0.3943 | 1.447 | 17.8914 | 0.92274 | 195.726 | 0.6493 | 84.954
334.15 | 61 | 1.494 | 1476.59 | 0.01113 | 111.903 | 0.3976 | 1.494 | 18.452 | 0.92084 | 196.571 | 0.651 | 84.668
335.15 | 62 | 1.542 | 1473.13 | 0.01148 | 113.036 | 0.401 | 1.542 | 19.0269 | 0.91892 | 197.416 | 0.6528 | 84.38
336.15 | 63 | 1.591 | 1469.66 | 0.01184 | 114.17 | 0.4044 | 1.591 | 19.6165 | 0.91696 | 198.26 | 0.6545 | 84.09
337.15 | 64 | 1.641 | 1466.17 | 0.01221 | 115.306 | 0.4077 | 1.641 | 20.221 | 0.91497 | 199.103 | 0.6563 | 83.797
338.15 | 65 | 1.693 | 1462.67 | 0.01259 | 116.443 | 0.4111 | 1.693 | 20.8408 | 0.91294 | 199.945 | 0.658 | 83.502
339.15 | 66 | 1.745 | 1459.15 | 0.01298 | 117.582 | 0.4145 | 1.745 | 21.4761 | 0.91088 | 200.787 | 0.6598 | 83.205
340.15 | 67 | 1.799 | 1455.62 | 0.01338 | 118.722 | 0.4178 | 1.799 | 22.1274 | 0.90879 | 201.628 | 0.6615 | 82.905
341.15 | 68 | 1.855 | 1452.08 | 0.01379 | 119.865 | 0.4211 | 1.855 | 22.7949 | 0.90667 | 202.467 | 0.6633 | 82.603
342.15 | 69 | 1.912 | 1448.52 | 0.01421 | 121.008 | 0.4245 | 1.912 | 23.4791 | 0.90451 | 203.306 | 0.665 | 82.298
343.15 | 70 | 1.97 | 1444.94 | 0.01464 | 122.154 | 0.4278 | 1.97 | 24.1802 | 0.90232 | 204.144 | 0.6668 | 81.99
344.15 | 71 | 2.029 | 1441.35 | 0.01508 | 123.302 | 0.4311 | 2.029 | 24.8986 | 0.90009 | 204.982 | 0.6685 | 81.68
345.15 | 72 | 2.09 | 1437.75 | 0.01553 | 124.451 | 0.4345 | 2.09 | 25.6348 | 0.89783 | 205.818 | 0.6702 | 81.367
346.15 | 73 | 2.152 | 1434.12 | 0.01599 | 125.602 | 0.4378 | 2.152 | 26.389 | 0.89553 | 206.653 | 0.6719 | 81.051
347.15 | 74 | 2.216 | 1430.49 | 0.01647 | 126.755 | 0.4411 | 2.216 | 27.1618 | 0.8932 | 207.487 | 0.6737 | 80.733
348.15 | 75 | 2.281 | 1426.84 | 0.01695 | 127.909 | 0.4444 | 2.281 | 27.9534 | 0.89083 | 208.321 | 0.6754 | 80.411
349.15 | 76 | 2.347 | 1423.17 | 0.01745 | 129.066 | 0.4477 | 2.347 | 28.7644 | 0.88843 | 209.153 | 0.6771 | 80.087
350.15 | 77 | 2.415 | 1419.48 | 0.01796 | 130.224 | 0.451 | 2.415 | 29.5951 | 0.88599 | 209.984 | 0.6788 | 79.76
351.15 | 78 | 2.485 | 1415.78 | 0.01848 | 131.385 | 0.4543 | 2.485 | 30.446 | 0.88351 | 210.814 | 0.6805 | 79.429
352.15 | 79 | 2.556 | 1412.06 | 0.01901 | 132.547 | 0.4576 | 2.556 | 31.3175 | 0.881 | 211.643 | 0.6822 | 79.096
353.15 | 80 | 2.629 | 1408.33 | 0.01956 | 133.712 | 0.4609 | 2.629 | 32.2101 | 0.87845 | 212.471 | 0.6839 | 78.759
354.15 | 81 | 2.703 | 1404.57 | 0.02012 | 134.878 | 0.4642 | 2.703 | 33.1242 | 0.87586 | 213.297 | 0.6856 | 78.419
355.15 | 82 | 2.779 | 1400.8 | 0.0207 | 136.047 | 0.4674 | 2.779 | 34.0604 | 0.87323 | 214.123 | 0.6873 | 78.076
356.15 | 83 | 2.856 | 1397.01 | 0.02128 | 137.218 | 0.4707 | 2.856 | 35.0192 | 0.87056 | 214.947 | 0.689 | 77.73
357.15 | 84 | 2.936 | 1393.21 | 0.02189 | 138.39 | 0.474 | 2.936 | 36.001 | 0.86786 | 215.77 | 0.6907 | 77.38
358.15 | 85 | 3.016 | 1389.38 | 0.0225 | 139.565 | 0.4773 | 3.016 | 37.0064 | 0.86511 | 216.592 | 0.6923 | 77.026
359.15 | 86 | 3.099 | 1385.54 | 0.02313 | 140.743 | 0.4805 | 3.099 | 38.036 | 0.86233 | 217.412 | 0.694 | 76.67
360.15 | 87 | 3.183 | 1381.67 | 0.02378 | 141.922 | 0.4838 | 3.183 | 39.0902 | 0.85951 | 218.231 | 0.6957 | 76.309
361.15 | 88 | 3.269 | 1377.79 | 0.02444 | 143.104 | 0.4871 | 3.269 | 40.1698 | 0.85664 | 219.049 | 0.6973 | 75.945
362.15 | 89 | 3.357 | 1373.89 | 0.02511 | 144.288 | 0.4903 | 3.357 | 41.2752 | 0.85374 | 219.865 | 0.699 | 75.577
363.15 | 90 | 3.447 | 1369.96 | 0.02581 | 145.475 | 0.4936 | 3.447 | 42.4072 | 0.85079 | 220.68 | 0.7007 | 75.205
364.15 | 91 | 3.538 | 1366.02 | 0.02652 | 146.664 | 0.4968 | 3.538 | 43.5662 | 0.8478 | 221.493 | 0.7023 | 74.83
365.15 | 92 | 3.632 | 1362.05 | 0.02724 | 147.855 | 0.5001 | 3.632 | 44.7531 | 0.84477 | 222.305 | 0.704 | 74.45
366.15 | 93 | 3.727 | 1358.06 | 0.02798 | 149.049 | 0.5033 | 3.727 | 45.9684 | 0.8417 | 223.116 | 0.7056 | 74.066
367.15 | 94 | 3.824 | 1354.05 | 0.02874 | 150.246 | 0.5066 | 3.824 | 47.2129 | 0.83859 | 223.924 | 0.7072 | 73.679
368.15 | 95 | 3.923 | 1350.02 | 0.02952 | 151.445 | 0.5098 | 3.923 | 48.4873 | 0.83543 | 224.731 | 0.7089 | 73.286
369.15 | 96 | 4.024 | 1345.96 | 0.03032 | 152.646 | 0.513 | 4.024 | 49.7923 | 0.83222 | 225.536 | 0.7105 | 72.89
370.15 | 97 | 4.127 | 1341.88 | 0.03113 | 153.851 | 0.5163 | 4.127 | 51.1287 | 0.82898 | 226.34 | 0.7121 | 72.489
371.15 | 98 | 4.232 | 1337.78 | 0.03197 | 155.058 | 0.5195 | 4.232 | 52.4973 | 0.82568 | 227.142 | 0.7137 | 72.084
372.15 | 99 | 4.339 | 1333.64 | 0.03282 | 156.268 | 0.5227 | 4.339 | 53.8989 | 0.82234 | 227.942 | 0.7153 | 71.674
373.15 | 100 | 4.449 | 1329.49 | 0.0337 | 157.481 | 0.526 | 4.449 | 55.3345 | 0.81896 | 228.74 | 0.7169 | 71.259
374.15 | 101 | 4.56 | 1325.3 | 0.03459 | 158.697 | 0.5292 | 4.56 | 56.8047 | 0.81553 | 229.536 | 0.7185 | 70.84
375.15 | 102 | 4.673 | 1321.09 | 0.03551 | 159.915 | 0.5324 | 4.673 | 58.3107 | 0.81205 | 230.33 | 0.7201 | 70.415
376.15 | 103 | 4.789 | 1316.85 | 0.03645 | 161.137 | 0.5357 | 4.789 | 59.8534 | 0.80853 | 231.123 | 0.7217 | 69.985
377.15 | 104 | 4.906 | 1312.58 | 0.03741 | 162.362 | 0.5389 | 4.906 | 61.4336 | 0.80495 | 231.913 | 0.7233 | 69.551
378.15 | 105 | 5.026 | 1308.28 | 0.03839 | 163.59 | 0.5421 | 5.026 | 63.0526 | 0.80133 | 232.701 | 0.7249 | 69.111
379.15 | 106 | 5.148 | 1303.95 | 0.0394 | 164.821 | 0.5454 | 5.148 | 64.7112 | 0.79765 | 233.486 | 0.7265 | 68.665
380.15 | 107 | 5.273 | 1299.58 | 0.04043 | 166.055 | 0.5486 | 5.273 | 66.4108 | 0.79393 | 234.27 | 0.728 | 68.214
381.15 | 108 | 5.4 | 1295.18 | 0.04149 | 167.293 | 0.5518 | 5.4 | 68.1523 | 0.79016 | 235.051 | 0.7296 | 67.758
382.15 | 109 | 5.529 | 1290.75 | 0.04257 | 168.534 | 0.555 | 5.529 | 69.937 | 0.78633 | 235.83 | 0.7311 | 67.295
383.15 | 110 | 5.66 | 1286.28 | 0.04368 | 169.779 | 0.5583 | 5.66 | 71.7663 | 0.78245 | 236.606 | 0.7327 | 66.827
384.15 | 111 | 5.794 | 1281.78 | 0.04481 | 171.027 | 0.5615 | 5.794 | 73.6412 | 0.77852 | 237.38 | 0.7342 | 66.352
385.15 | 112 | 5.93 | 1277.23 | 0.04597 | 172.279 | 0.5647 | 5.93 | 75.5634 | 0.77453 | 238.151 | 0.7357 | 65.872
386.15 | 113 | 6.069 | 1272.65 | 0.04716 | 173.535 | 0.5679 | 6.069 | 77.5341 | 0.77049 | 238.919 | 0.7373 | 65.384
387.15 | 114 | 6.21 | 1268.02 | 0.04838 | 174.794 | 0.5712 | 6.21 | 79.5548 | 0.76639 | 239.685 | 0.7388 | 64.89
388.15 | 115 | 6.353 | 1263.36 | 0.04963 | 176.058 | 0.5744 | 6.353 | 81.6272 | 0.76223 | 240.447 | 0.7403 | 64.39
389.15 | 116 | 6.499 | 1258.64 | 0.05092 | 177.325 | 0.5776 | 6.499 | 83.7529 | 0.75802 | 241.207 | 0.7418 | 63.882
390.15 | 117 | 6.648 | 1253.88 | 0.05223 | 178.597 | 0.5809 | 6.648 | 85.9335 | 0.75375 | 241.964 | 0.7433 | 63.367
391.15 | 118 | 6.799 | 1249.07 | 0.05358 | 179.872 | 0.5841 | 6.799 | 88.1708 | 0.74941 | 242.717 | 0.7448 | 62.845
392.15 | 119 | 6.953 | 1244.22 | 0.05496 | 181.152 | 0.5873 | 6.953 | 90.4668 | 0.74502 | 243.468 | 0.7462 | 62.315
393.15 | 120 | 7.11 | 1239.3 | 0.05638 | 182.437 | 0.5906 | 7.11 | 92.8234 | 0.74056 | 244.214 | 0.7477 | 61.778
394.15 | 121 | 7.269 | 1234.34 | 0.05783 | 183.726 | 0.5938 | 7.269 | 95.2427 | 0.73604 | 244.958 | 0.7492 | 61.232
395.15 | 122 | 7.431 | 1229.31 | 0.05932 | 185.02 | 0.5971 | 7.431 | 97.7269 | 0.73146 | 245.698 | 0.7506 | 60.678
396.15 | 123 | 7.596 | 1224.22 | 0.06085 | 186.318 | 0.6003 | 7.596 | 100.2782 | 0.72681 | 246.434 | 0.7521 | 60.115
397.15 | 124 | 7.763 | 1219.08 | 0.06242 | 187.622 | 0.6036 | 7.763 | 102.8992 | 0.72209 | 247.166 | 0.7535 | 59.544
398.15 | 125 | 7.933 | 1213.86 | 0.06403 | 188.931 | 0.6068 | 7.933 | 105.5923 | 0.7173 | 247.894 | 0.7549 | 58.963
399.15 | 126 | 8.106 | 1208.58 | 0.06569 | 190.244 | 0.6101 | 8.106 | 108.3603 | 0.71244 | 248.618 | 0.7563 | 58.373
400.15 | 127 | 8.282 | 1203.22 | 0.06739 | 191.564 | 0.6133 | 8.282 | 111.2061 | 0.70751 | 249.338 | 0.7577 | 57.774
401.15 | 128 | 8.461 | 1197.78 | 0.06914 | 192.889 | 0.6166 | 8.461 | 114.1327 | 0.70251 | 250.053 | 0.7591 | 57.164
402.15 | 129 | 8.643 | 1192.27 | 0.07093 | 194.219 | 0.6199 | 8.643 | 117.1434 | 0.69743 | 250.763 | 0.7605 | 56.544
403.15 | 130 | 8.828 | 1186.67 | 0.07278 | 195.556 | 0.6232 | 8.828 | 120.2415 | 0.69227 | 251.469 | 0.7618 | 55.913
404.15 | 131 | 9.016 | 1180.98 | 0.07468 | 196.899 | 0.6264 | 9.016 | 123.4308 | 0.68703 | 252.169 | 0.7632 | 55.27
405.15 | 132 | 9.207 | 1175.19 | 0.07663 | 198.248 | 0.6297 | 9.207 | 126.7151 | 0.6817 | 252.864 | 0.7645 | 54.616
406.15 | 133 | 9.401 | 1169.31 | 0.07864 | 199.604 | 0.633 | 9.401 | 130.0986 | 0.6763 | 253.554 | 0.7659 | 53.95
407.15 | 134 | 9.598 | 1163.32 | 0.08071 | 200.967 | 0.6363 | 9.598 | 133.5858 | 0.6708 | 254.238 | 0.7672 | 53.272
408.15 | 135 | 9.798 | 1157.22 | 0.08284 | 202.336 | 0.6397 | 9.798 | 137.1814 | 0.66521 | 254.916 | 0.7685 | 52.58
409.15 | 136 | 10.002 | 1151 | 0.08504 | 203.714 | 0.643 | 10.002 | 140.8906 | 0.65953 | 255.588 | 0.7698 | 51.874
410.15 | 137 | 10.208 | 1144.65 | 0.08731 | 205.099 | 0.6463 | 10.208 | 144.7189 | 0.65376 | 256.253 | 0.771 | 51.154
411.15 | 138 | 10.418 | 1138.17 | 0.08965 | 206.492 | 0.6497 | 10.418 | 148.6724 | 0.64788 | 256.911 | 0.7723 | 50.419
412.15 | 139 | 10.632 | 1131.55 | 0.09206 | 207.893 | 0.653 | 10.632 | 152.7573 | 0.6419 | 257.562 | 0.7735 | 49.669
413.15 | 140 | 10.848 | 1124.78 | 0.09455 | 209.303 | 0.6564 | 10.848 | 156.9808 | 0.63581 | 258.205 | 0.7748 | 48.902
414.15 | 141 | 11.068 | 1117.84 | 0.09713 | 210.723 | 0.6598 | 11.068 | 161.3504 | 0.62961 | 258.84 | 0.776 | 48.117
415.15 | 142 | 11.292 | 1110.74 | 0.0998 | 212.152 | 0.6632 | 11.292 | 165.8745 | 0.6233 | 259.467 | 0.7771 | 47.315
416.15 | 143 | 11.518 | 1103.44 | 0.10255 | 213.591 | 0.6666 | 11.518 | 170.5621 | 0.61686 | 260.085 | 0.7783 | 46.493
417.15 | 144 | 11.749 | 1095.95 | 0.10541 | 215.041 | 0.67 | 11.749 | 175.4231 | 0.61029 | 260.693 | 0.7794 | 45.651
418.15 | 145 | 11.983 | 1088.25 | 0.10838 | 216.502 | 0.6734 | 11.983 | 180.4686 | 0.60359 | 261.291 | 0.7806 | 44.788
419.15 | 146 | 12.22 | 1080.31 | 0.11145 | 217.976 | 0.6769 | 12.22 | 185.7106 | 0.59674 | 261.878 | 0.7816 | 43.902
420.15 | 147 | 12.461 | 1072.13 | 0.11465 | 219.462 | 0.6804 | 12.461 | 191.1626 | 0.58975 | 262.453 | 0.7827 | 42.992
421.15 | 148 | 12.706 | 1063.68 | 0.11797 | 220.961 | 0.6839 | 12.706 | 196.8397 | 0.5826 | 263.017 | 0.7838 | 42.056
422.15 | 149 | 12.954 | 1054.93 | 0.12144 | 222.475 | 0.6874 | 12.954 | 202.7587 | 0.57528 | 263.567 | 0.7848 | 41.092
423.15 | 150 | 13.206 | 1045.87 | 0.12505 | 224.004 | 0.691 | 13.206 | 208.9385 | 0.56778 | 264.102 | 0.7857 | 40.098
424.15 | 151 | 13.462 | 1036.46 | 0.12883 | 225.55 | 0.6946 | 13.462 | 215.4008 | 0.56009 | 264.623 | 0.7867 | 39.073
425.15 | 152 | 13.73 | 1026.8 | 0.13284 | 227.108 | 0.6982 | 13.73 | 222.558 | 0.5516 | 265.099 | 0.7875 | 37.991
426.15 | 153 | 13.994 | 1016.61 | 0.13698 | 228.691 | 0.7018 | 13.994 | 229.689 | 0.54346 | 265.582 | 0.7884 | 36.891
427.15 | 154 | 14.262 | 1005.95 | 0.14134 | 230.294 | 0.7055 | 14.262 | 237.193 | 0.53507 | 266.045 | 0.7892 | 35.751
428.15 | 155 | 14.533 | 994.78 | 0.14592 | 231.921 | 0.7092 | 14.533 | 245.107 | 0.52642 | 266.486 | 0.79 | 34.565
429.15 | 156 | 14.808 | 983.04 | 0.15077 | 233.574 | 0.713 | 14.808 | 253.479 | 0.51747 | 266.902 | 0.7907 | 33.328
430.15 | 157 | 15.088 | 970.65 | 0.1559 | 235.254 | 0.7169 | 15.088 | 262.364 | 0.50819 | 267.291 | 0.7913 | 32.037
431.15 | 158 | 15.371 | 957.53 | 0.16137 | 236.967 | 0.7208 | 15.371 | 271.835 | 0.49854 | 267.647 | 0.7919 | 30.68
432.15 | 159 | 15.659 | 943.57 | 0.16721 | 238.717 | 0.7247 | 15.659 | 281.966 | 0.48849 | 267.968 | 0.7924 | 29.251
433.15 | 160 | 15.951 | 928.64 | 0.17348 | 240.507 | 0.7288 | 15.951 | 292.883 | 0.47794 | 268.245 | 0.7928 | 27.738
434.15 | 161 | 16.246 | 912.57 | 0.18027 | 242.347 | 0.7329 | 16.246 | 304.711 | 0.46683 | 268.474 | 0.7931 | 26.127
435.15 | 162 | 16.547 | 895.12 | 0.18767 | 244.246 | 0.7372 | 16.547 | 317.642 | 0.45505 | 268.643 | 0.7933 | 24.397
436.15 | 163 | 16.851 | 875.99 | 0.19583 | 246.215 | 0.7416 | 16.851 | 331.949 | 0.44243 | 268.738 | 0.7933 | 22.523

## Compressed Liq & Superheat Vap
Thermodynamic Properties of the Compressed Liquid and Superheated Vapor for 3MTM NovecTM 1230 Fire Protection Fluid
T | -40 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.163 | 1766.033 | 1766.07 | 1766.106 | 1766.143 | 1766.179 | 1766.216 | 1766.252 | 1766.289 | 1766.362 | 1766.725 | 1767.088 | 1767.449 | 1767.81 | 1768.706 | 1769.596 | 1773.092 | 1776.49 | 1779.795 | 1783.011
V |  | kg/m3 | 6.125 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000566 | 0.000565 | 0.000565 | 0.000564 | 0.000563 | 0.000562 | 0.000561
Z |  |  | 0.99861 | 0.0009 | 0.001801 | 0.002701 | 0.003602 | 0.004502 | 0.005402 | 0.006303 | 0.007203 | 0.009003 | 0.018003 | 0.027 | 0.035994 | 0.044985 | 0.067449 | 0.089894 | 0.17949 | 0.2688 | 0.35785 | 0.44663
H |  | kJ/kg | 109.342 | 0.004 | 0.008 | 0.012 | 0.016 | 0.02 | 0.024 | 0.028 | 0.032 | 0.041 | 0.082 | 0.123 | 0.164 | 0.205 | 0.308 | 0.412 | 0.826 | 1.243 | 1.662 | 2.083
S |  | kJ/kg*K | 0.469 | 0 | 0 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0001 | -0.0002 | -0.0002 | -0.0003 | -0.0003 | -0.0005 | -0.0006 | -0.0012 | -0.0018 | -0.0023 | -0.0029
CP |  | kJ/kg*K | 0.8737 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 1.0812 | 1.0812 | 1.0811 | 1.081 | 1.0809 | 1.0808 | 1.0805 | 1.0802 | 1.0791 | 1.0781 | 1.0771 | 1.0762
CP/CV |  |  | 1.0312 | 1.09 | 1.09 | 1.09 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 1.0897 | 1.0896 | 1.0894 | 1.0893 | 1.089 | 1.0886 | 1.0873 | 1.0861 | 1.0849 | 1.0838
CS |  | m/s | 79.4187 | 587.9186 | 588.0053 | 588.0963 | 588.1859 | 588.2785 | 588.3683 | 588.4581 | 588.548 | 588.7279 | 589.6285 | 590.528 | 591.4278 | 592.3235 | 594.5657 | 596.8011 | 605.6963 | 614.5171 | 623.268 | 631.9513
T | -35 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.16 | 1754.381 | 1754.42 | 1754.458 | 1754.497 | 1754.536 | 1754.575 | 1754.614 | 1754.652 | 1754.73 | 1755.117 | 1755.502 | 1755.887 | 1756.27 | 1757.223 | 1758.169 | 1761.883 | 1765.489 | 1768.993 | 1772.401
V |  | kg/m3 | 6.2569 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.00057 | 0.000569 | 0.000569 | 0.000569 | 0.000568 | 0.000566 | 0.000565 | 0.000564
Z |  |  | 0.99869 | 0.000887 | 0.001773 | 0.002659 | 0.003546 | 0.004432 | 0.005319 | 0.006205 | 0.007091 | 0.008864 | 0.017724 | 0.026581 | 0.035434 | 0.044285 | 0.066397 | 0.088488 | 0.17666 | 0.26454 | 0.35213 | 0.43945
H |  | kJ/kg | 113.711 | 5.411 | 5.415 | 5.419 | 5.423 | 5.427 | 5.431 | 5.435 | 5.439 | 5.447 | 5.488 | 5.528 | 5.569 | 5.61 | 5.711 | 5.813 | 6.222 | 6.634 | 7.048 | 7.464
S |  | kJ/kg*K | 0.4876 | 0.0229 | 0.0229 | 0.0229 | 0.0229 | 0.0229 | 0.0229 | 0.0229 | 0.0229 | 0.0228 | 0.0228 | 0.0227 | 0.0227 | 0.0226 | 0.0224 | 0.0223 | 0.0217 | 0.0211 | 0.0205 | 0.0199
CP |  | kJ/kg*K | 0.8737 | 1.0816 | 1.0816 | 1.0816 | 1.0816 | 1.0815 | 1.0815 | 1.0815 | 1.0815 | 1.0815 | 1.0814 | 1.0812 | 1.0811 | 1.081 | 1.0807 | 1.0804 | 1.0792 | 1.0781 | 1.0771 | 1.0761
CP/CV |  |  | 1.0312 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 1.0922 | 1.0922 | 1.0922 | 1.092 | 1.0919 | 1.0917 | 1.0916 | 1.0912 | 1.0909 | 1.0895 | 1.0882 | 1.0869 | 1.0857
CS |  | m/s | 80.2717 | 568.5906 | 568.6826 | 568.7709 | 568.8618 | 568.9527 | 569.045 | 569.1322 | 569.2246 | 569.4045 | 570.3091 | 571.2138 | 572.1172 | 573.0179 | 575.2666 | 577.5125 | 586.4382 | 595.2884 | 604.0604 | 612.7586
T | -30 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.157 | 1742.458 | 1742.499 | 1742.541 | 1742.582 | 1742.623 | 1742.664 | 1742.706 | 1742.747 | 1742.829 | 1743.24 | 1743.65 | 1744.059 | 1744.466 | 1745.479 | 1746.484 | 1750.427 | 1754.253 | 1757.967 | 1761.576
V |  | kg/m3 | 6.3887 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000574 | 0.000573 | 0.000573 | 0.000573 | 0.000573 | 0.000571 | 0.00057 | 0.000569 | 0.000568
Z |  |  | 0.99876 | 0.000873 | 0.001747 | 0.00262 | 0.003493 | 0.004366 | 0.005239 | 0.006113 | 0.006986 | 0.008732 | 0.01746 | 0.026184 | 0.034906 | 0.043623 | 0.065402 | 0.087161 | 0.17399 | 0.2605 | 0.34671 | 0.43264
H |  | kJ/kg | 118.08 | 10.82 | 10.824 | 10.828 | 10.832 | 10.836 | 10.84 | 10.844 | 10.848 | 10.856 | 10.896 | 10.936 | 10.976 | 11.016 | 11.116 | 11.216 | 11.619 | 12.025 | 12.433 | 12.845
S |  | kJ/kg*K | 0.5057 | 0.0454 | 0.0454 | 0.0454 | 0.0454 | 0.0454 | 0.0454 | 0.0453 | 0.0453 | 0.0453 | 0.0453 | 0.0452 | 0.0451 | 0.0451 | 0.0449 | 0.0447 | 0.0441 | 0.0435 | 0.0429 | 0.0423
CP |  | kJ/kg*K | 0.8739 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 1.082 | 1.082 | 1.0819 | 1.0817 | 1.0816 | 1.0815 | 1.0812 | 1.0808 | 1.0796 | 1.0784 | 1.0773 | 1.0762
CP/CV |  |  | 1.0312 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 1.0946 | 1.0946 | 1.0946 | 1.0944 | 1.0943 | 1.0941 | 1.094 | 1.0936 | 1.0932 | 1.0917 | 1.0903 | 1.0889 | 1.0876
CS |  | m/s | 81.1153 | 549.8633 | 549.9546 | 550.0459 | 550.1373 | 550.2277 | 550.3192 | 550.4086 | 550.4991 | 550.6815 | 551.5886 | 552.498 | 553.4061 | 554.3117 | 556.5722 | 558.8284 | 567.7938 | 576.6748 | 585.4731 | 594.1919
T | -25 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.153 | 1730.263 | 1730.307 | 1730.351 | 1730.394 | 1730.438 | 1730.482 | 1730.526 | 1730.57 | 1730.657 | 1731.094 | 1731.53 | 1731.964 | 1732.397 | 1733.473 | 1734.54 | 1738.725 | 1742.782 | 1746.716 | 1750.535
V |  | kg/m3 | 6.5205 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000578 | 0.000577 | 0.000577 | 0.000577 | 0.000577 | 0.000575 | 0.000574 | 0.000573 | 0.000571
Z |  |  | 0.99883 | 0.000861 | 0.001722 | 0.002583 | 0.003443 | 0.004304 | 0.005165 | 0.006025 | 0.006886 | 0.008607 | 0.017211 | 0.02581 | 0.034406 | 0.042999 | 0.064464 | 0.085906 | 0.17146 | 0.25668 | 0.34158 | 0.42618
H |  | kJ/kg | 122.45 | 16.233 | 16.237 | 16.241 | 16.245 | 16.248 | 16.252 | 16.256 | 16.26 | 16.268 | 16.307 | 16.346 | 16.386 | 16.425 | 16.523 | 16.622 | 17.018 | 17.418 | 17.821 | 18.226
S |  | kJ/kg*K | 0.5235 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0674 | 0.0673 | 0.0672 | 0.0672 | 0.0671 | 0.0669 | 0.0667 | 0.0661 | 0.0654 | 0.0648 | 0.0642
CP |  | kJ/kg*K | 0.8743 | 1.083 | 1.083 | 1.0829 | 1.0829 | 1.0829 | 1.0829 | 1.0829 | 1.0829 | 1.0828 | 1.0827 | 1.0826 | 1.0824 | 1.0823 | 1.0819 | 1.0816 | 1.0802 | 1.0789 | 1.0777 | 1.0766
CP/CV |  |  | 1.0312 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 1.0969 | 1.0967 | 1.0966 | 1.0964 | 1.096 | 1.0955 | 1.0939 | 1.0924 | 1.0909 | 1.0896
CS |  | m/s | 81.9498 | 531.7003 | 531.7914 | 531.8836 | 531.9748 | 532.0671 | 532.1585 | 532.2509 | 532.3414 | 532.5246 | 533.439 | 534.3535 | 535.2638 | 536.1761 | 538.4499 | 540.7181 | 549.727 | 558.6467 | 567.4754 | 576.2231
T | -20 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.15 | 1717.792 | 1717.839 | 1717.885 | 1717.932 | 1717.979 | 1718.025 | 1718.072 | 1718.118 | 1718.211 | 1718.676 | 1719.139 | 1719.6 | 1720.06 | 1721.202 | 1722.335 | 1726.775 | 1731.074 | 1735.24 | 1739.28
V |  | kg/m3 | 6.6523 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000582 | 0.000581 | 0.000581 | 0.000581 | 0.000579 | 0.000578 | 0.000576 | 0.000575
Z |  |  | 0.99889 | 0.000849 | 0.001698 | 0.002547 | 0.003396 | 0.004245 | 0.005094 | 0.005943 | 0.006792 | 0.00849 | 0.016976 | 0.025458 | 0.033936 | 0.04241 | 0.063578 | 0.084723 | 0.16907 | 0.25306 | 0.33672 | 0.42007
H |  | kJ/kg | 126.823 | 21.65 | 21.654 | 21.658 | 21.662 | 21.666 | 21.67 | 21.673 | 21.677 | 21.685 | 21.723 | 21.762 | 21.8 | 21.839 | 21.935 | 22.032 | 22.421 | 22.815 | 23.211 | 23.611
S |  | kJ/kg*K | 0.541 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.0889 | 0.0888 | 0.0888 | 0.0887 | 0.0885 | 0.0883 | 0.0876 | 0.087 | 0.0863 | 0.0857
CP |  | kJ/kg*K | 0.8749 | 1.0841 | 1.0841 | 1.0841 | 1.0841 | 1.084 | 1.084 | 1.084 | 1.084 | 1.084 | 1.0838 | 1.0836 | 1.0835 | 1.0833 | 1.0829 | 1.0826 | 1.0811 | 1.0797 | 1.0784 | 1.0772
CP/CV |  |  | 1.0311 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 1.0995 | 1.0993 | 1.0991 | 1.0989 | 1.0984 | 1.098 | 1.0962 | 1.0946 | 1.093 | 1.0915
CS |  | m/s | 82.7754 | 514.0748 | 514.1667 | 514.2587 | 514.3499 | 514.443 | 514.5352 | 514.6275 | 514.719 | 514.905 | 515.8247 | 516.7439 | 517.6616 | 518.5804 | 520.8689 | 523.1504 | 532.2136 | 541.174 | 550.0406 | 558.8199
T | -15 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.147 | 1705.043 | 1705.093 | 1705.142 | 1705.192 | 1705.242 | 1705.291 | 1705.341 | 1705.39 | 1705.489 | 1705.982 | 1706.474 | 1706.964 | 1707.452 | 1708.665 | 1709.867 | 1714.576 | 1719.13 | 1723.539 | 1727.81
V |  | kg/m3 | 6.7841 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000586 | 0.000585 | 0.000585 | 0.000583 | 0.000582 | 0.00058 | 0.000579
Z |  |  | 0.99895 | 0.000838 | 0.001676 | 0.002514 | 0.003352 | 0.00419 | 0.005028 | 0.005866 | 0.006704 | 0.008379 | 0.016755 | 0.025126 | 0.033492 | 0.041855 | 0.062744 | 0.083607 | 0.16681 | 0.24965 | 0.33213 | 0.41428
H |  | kJ/kg | 131.199 | 27.074 | 27.078 | 27.082 | 27.086 | 27.089 | 27.093 | 27.097 | 27.101 | 27.108 | 27.146 | 27.183 | 27.221 | 27.259 | 27.353 | 27.448 | 27.83 | 28.216 | 28.606 | 28.999
S |  | kJ/kg*K | 0.5581 | 0.1103 | 0.1102 | 0.1102 | 0.1102 | 0.1102 | 0.1102 | 0.1102 | 0.1102 | 0.1102 | 0.1101 | 0.11 | 0.11 | 0.1099 | 0.1097 | 0.1095 | 0.1088 | 0.1081 | 0.1074 | 0.1068
CP |  | kJ/kg*K | 0.8756 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 1.0852 | 1.085 | 1.0849 | 1.0847 | 1.0843 | 1.0839 | 1.0823 | 1.0808 | 1.0794 | 1.0781
CP/CV |  |  | 1.0311 | 1.1025 | 1.1025 | 1.1025 | 1.1024 | 1.1024 | 1.1024 | 1.1024 | 1.1024 | 1.1023 | 1.1021 | 1.1019 | 1.1017 | 1.1015 | 1.101 | 1.1005 | 1.0986 | 1.0968 | 1.0952 | 1.0936
CS |  | m/s | 83.5924 | 496.9529 | 497.0454 | 497.1388 | 497.2322 | 497.3257 | 497.4185 | 497.5106 | 497.6043 | 497.7897 | 498.7173 | 499.6433 | 500.5693 | 501.4942 | 503.7981 | 506.097 | 515.2165 | 524.2281 | 533.1381 | 541.955
T | -10 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.145 | 1692.014 | 1692.066 | 1692.119 | 1692.172 | 1692.224 | 1692.277 | 1692.329 | 1692.382 | 1692.487 | 1693.011 | 1693.533 | 1694.053 | 1694.571 | 1695.859 | 1697.135 | 1702.127 | 1706.95 | 1711.613 | 1716.127
V |  | kg/m3 | 6.9159 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.000591 | 0.00059 | 0.00059 | 0.00059 | 0.00059 | 0.000589 | 0.000588 | 0.000586 | 0.000584 | 0.000583
Z |  |  | 0.99901 | 0.000828 | 0.001655 | 0.002483 | 0.003311 | 0.004138 | 0.004966 | 0.005793 | 0.006621 | 0.008276 | 0.016547 | 0.024813 | 0.033076 | 0.041333 | 0.061958 | 0.082557 | 0.16469 | 0.24642 | 0.32778 | 0.40879
H |  | kJ/kg | 135.58 | 32.506 | 32.51 | 32.513 | 32.517 | 32.521 | 32.524 | 32.528 | 32.532 | 32.539 | 32.576 | 32.612 | 32.649 | 32.686 | 32.778 | 32.871 | 33.245 | 33.623 | 34.005 | 34.392
S |  | kJ/kg*K | 0.5749 | 0.1311 | 0.1311 | 0.1311 | 0.1311 | 0.1311 | 0.1311 | 0.131 | 0.131 | 0.131 | 0.1309 | 0.1309 | 0.1308 | 0.1307 | 0.1305 | 0.1303 | 0.1296 | 0.1288 | 0.1281 | 0.1275
CP |  | kJ/kg*K | 0.8765 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 1.0869 | 1.0867 | 1.0865 | 1.0863 | 1.0859 | 1.0854 | 1.0837 | 1.0821 | 1.0806 | 1.0792
CP/CV |  |  | 1.0311 | 1.1053 | 1.1053 | 1.1052 | 1.1052 | 1.1052 | 1.1052 | 1.1052 | 1.1051 | 1.1051 | 1.1049 | 1.1046 | 1.1044 | 1.1042 | 1.1037 | 1.1031 | 1.1011 | 1.0992 | 1.0974 | 1.0957
CS |  | m/s | 84.4011 | 480.3114 | 480.4053 | 480.5 | 480.5927 | 480.6868 | 480.7796 | 480.874 | 480.9684 | 481.1554 | 482.0904 | 483.0255 | 483.9575 | 484.8894 | 487.2135 | 489.5282 | 498.714 | 507.7825 | 516.7426 | 525.5999
T | -5 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.142 | 1678.7 | 1678.756 | 1678.812 | 1678.868 | 1678.924 | 1678.98 | 1679.035 | 1679.091 | 1679.203 | 1679.759 | 1680.313 | 1680.866 | 1681.416 | 1682.782 | 1684.136 | 1689.427 | 1694.533 | 1699.464 | 1704.231
V |  | kg/m3 | 7.0476 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000596 | 0.000595 | 0.000595 | 0.000595 | 0.000595 | 0.000594 | 0.000594 | 0.000592 | 0.00059 | 0.000588 | 0.000587
Z |  |  | 0.99906 | 0.000818 | 0.001636 | 0.002454 | 0.003272 | 0.00409 | 0.004908 | 0.005725 | 0.006543 | 0.008178 | 0.016352 | 0.02452 | 0.032684 | 0.040843 | 0.061221 | 0.081569 | 0.16269 | 0.24338 | 0.32368 | 0.40361
H |  | kJ/kg | 139.965 | 37.947 | 37.951 | 37.954 | 37.958 | 37.961 | 37.965 | 37.969 | 37.972 | 37.979 | 38.015 | 38.051 | 38.087 | 38.122 | 38.212 | 38.303 | 38.667 | 39.037 | 39.412 | 39.791
S |  | kJ/kg*K | 0.5914 | 0.1516 | 0.1516 | 0.1516 | 0.1515 | 0.1515 | 0.1515 | 0.1515 | 0.1515 | 0.1515 | 0.1514 | 0.1513 | 0.1513 | 0.1512 | 0.151 | 0.1508 | 0.15 | 0.1492 | 0.1485 | 0.1478
CP |  | kJ/kg*K | 0.8775 | 1.0893 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 1.0891 | 1.0891 | 1.0891 | 1.0889 | 1.0887 | 1.0885 | 1.0883 | 1.0878 | 1.0873 | 1.0854 | 1.0837 | 1.0821 | 1.0805
CP/CV |  |  | 1.031 | 1.1082 | 1.1082 | 1.1081 | 1.1081 | 1.1081 | 1.1081 | 1.108 | 1.108 | 1.108 | 1.1077 | 1.1075 | 1.1072 | 1.107 | 1.1064 | 1.1058 | 1.1036 | 1.1016 | 1.0996 | 1.0978
CS |  | m/s | 85.2018 | 464.1236 | 464.218 | 464.3137 | 464.4083 | 464.5023 | 464.5977 | 464.6912 | 464.7855 | 464.9744 | 465.9199 | 466.8618 | 467.8033 | 468.7442 | 471.0872 | 473.4237 | 482.6828 | 491.8148 | 500.8281 | 509.7345
T | 0 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.139 | 1.404 | 1665.159 | 1665.218 | 1665.278 | 1665.337 | 1665.396 | 1665.456 | 1665.515 | 1665.633 | 1666.224 | 1666.813 | 1667.399 | 1667.983 | 1669.432 | 1670.868 | 1676.476 | 1681.879 | 1687.091 | 1692.125
V |  | kg/m3 | 7.1794 | 0.7121 | 0.000601 | 0.000601 | 0.000601 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.000599 | 0.000598 | 0.000596 | 0.000595 | 0.000593 | 0.000591
Z |  |  | 0.9991 | 0.99098 | 0.001618 | 0.002427 | 0.003235 | 0.004044 | 0.004853 | 0.005661 | 0.00647 | 0.008087 | 0.016169 | 0.024246 | 0.032317 | 0.040384 | 0.060529 | 0.080643 | 0.1608 | 0.24051 | 0.31981 | 0.39871
H |  | kJ/kg | 144.355 | 144.19 | 43.403 | 43.406 | 43.41 | 43.413 | 43.416 | 43.42 | 43.423 | 43.43 | 43.465 | 43.5 | 43.534 | 43.569 | 43.657 | 43.744 | 44.099 | 44.46 | 44.826 | 45.198
S |  | kJ/kg*K | 0.6076 | 0.5467 | 0.1717 | 0.1717 | 0.1717 | 0.1717 | 0.1717 | 0.1717 | 0.1717 | 0.1716 | 0.1716 | 0.1715 | 0.1714 | 0.1713 | 0.1711 | 0.1709 | 0.1701 | 0.1693 | 0.1685 | 0.1678
CP |  | kJ/kg*K | 0.8788 | 0.8797 | 1.0916 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 1.0914 | 1.0914 | 1.0914 | 1.0911 | 1.0909 | 1.0907 | 1.0905 | 1.0899 | 1.0894 | 1.0874 | 1.0855 | 1.0838 | 1.0821
CP/CV |  |  | 1.031 | 1.0319 | 1.1112 | 1.1111 | 1.1111 | 1.1111 | 1.1111 | 1.111 | 1.111 | 1.111 | 1.1107 | 1.1104 | 1.1102 | 1.1099 | 1.1093 | 1.1086 | 1.1062 | 1.104 | 1.1019 | 1.0999
CS |  | m/s | 85.9945 | 85.3309 | 448.4599 | 448.555 | 448.6519 | 448.7471 | 448.8425 | 448.9385 | 449.0324 | 449.2244 | 450.1791 | 451.1311 | 452.0821 | 453.0314 | 455.3994 | 457.7556 | 467.0953 | 476.3005 | 485.3766 | 494.3351
T | 5 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.137 | 1.378 | 1651.272 | 1651.335 | 1651.398 | 1651.461 | 1651.524 | 1651.587 | 1651.65 | 1651.775 | 1652.403 | 1653.027 | 1653.65 | 1654.269 | 1655.807 | 1657.33 | 1663.271 | 1668.988 | 1674.496 | 1679.809
V |  | kg/m3 | 7.3111 | 0.72547 | 0.000606 | 0.000606 | 0.000606 | 0.000606 | 0.000606 | 0.000605 | 0.000605 | 0.000605 | 0.000605 | 0.000605 | 0.000605 | 0.000604 | 0.000604 | 0.000603 | 0.000601 | 0.000599 | 0.000597 | 0.000595
Z |  |  | 0.99915 | 0.99144 | 0.001601 | 0.002401 | 0.003201 | 0.004002 | 0.004802 | 0.005602 | 0.006402 | 0.008002 | 0.015998 | 0.023989 | 0.031975 | 0.039955 | 0.059882 | 0.079776 | 0.15904 | 0.23782 | 0.31616 | 0.39408
H |  | kJ/kg | 148.752 | 148.592 | 48.867 | 48.87 | 48.873 | 48.877 | 48.88 | 48.883 | 48.887 | 48.894 | 48.927 | 48.96 | 48.994 | 49.028 | 49.112 | 49.197 | 49.542 | 49.893 | 50.25 | 50.613
S |  | kJ/kg*K | 0.6236 | 0.5626 | 0.1915 | 0.1915 | 0.1915 | 0.1915 | 0.1915 | 0.1915 | 0.1915 | 0.1915 | 0.1914 | 0.1913 | 0.1912 | 0.1911 | 0.1909 | 0.1907 | 0.1898 | 0.189 | 0.1882 | 0.1874
CP |  | kJ/kg*K | 0.8801 | 0.881 | 1.0942 | 1.0942 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.094 | 1.094 | 1.0937 | 1.0935 | 1.0933 | 1.093 | 1.0924 | 1.0918 | 1.0897 | 1.0876 | 1.0857 | 1.084
CP/CV |  |  | 1.0309 | 1.0318 | 1.1143 | 1.1143 | 1.1143 | 1.1142 | 1.1142 | 1.1142 | 1.1141 | 1.1141 | 1.1138 | 1.1135 | 1.1132 | 1.1129 | 1.1122 | 1.1116 | 1.109 | 1.1065 | 1.1043 | 1.1022
CS |  | m/s | 86.7797 | 86.1442 | 433.1072 | 433.2041 | 433.3016 | 433.3982 | 433.4939 | 433.5907 | 433.6882 | 433.8804 | 434.8452 | 435.8086 | 436.7709 | 437.7304 | 440.1225 | 442.5048 | 451.9352 | 461.2168 | 470.361 | 479.378
T | 10 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.134 | 1.353 | 2.73 | 1637.157 | 1637.224 | 1637.291 | 1637.358 | 1637.425 | 1637.492 | 1637.625 | 1638.292 | 1638.955 | 1639.615 | 1640.273 | 1641.905 | 1643.519 | 1649.814 | 1655.861 | 1661.68 | 1667.285
V |  | kg/m3 | 7.4429 | 0.73883 | 0.36634 | 0.000611 | 0.000611 | 0.000611 | 0.000611 | 0.000611 | 0.000611 | 0.000611 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.000609 | 0.000608 | 0.000606 | 0.000604 | 0.000602 | 0.0006
Z |  |  | 0.99919 | 0.99186 | 0.98362 | 0.002377 | 0.00317 | 0.003962 | 0.004754 | 0.005547 | 0.006339 | 0.007923 | 0.01584 | 0.023751 | 0.031656 | 0.039555 | 0.059279 | 0.078967 | 0.15738 | 0.23529 | 0.31273 | 0.38972
H |  | kJ/kg | 153.157 | 153.001 | 152.825 | 54.348 | 54.351 | 54.355 | 54.358 | 54.361 | 54.364 | 54.371 | 54.403 | 54.435 | 54.467 | 54.5 | 54.581 | 54.663 | 54.996 | 55.337 | 55.684 | 56.038
S |  | kJ/kg*K | 0.6393 | 0.5783 | 0.5597 | 0.211 | 0.211 | 0.211 | 0.211 | 0.211 | 0.211 | 0.211 | 0.2109 | 0.2108 | 0.2107 | 0.2106 | 0.2104 | 0.2101 | 0.2092 | 0.2084 | 0.2075 | 0.2067
CP |  | kJ/kg*K | 0.8816 | 0.8825 | 0.8835 | 1.0971 | 1.0971 | 1.0971 | 1.097 | 1.097 | 1.097 | 1.0969 | 1.0966 | 1.0964 | 1.0961 | 1.0959 | 1.0952 | 1.0946 | 1.0922 | 1.09 | 1.0879 | 1.086
CP/CV |  |  | 1.0309 | 1.0317 | 1.0327 | 1.1176 | 1.1176 | 1.1175 | 1.1175 | 1.1175 | 1.1174 | 1.1174 | 1.117 | 1.1167 | 1.1164 | 1.1161 | 1.1154 | 1.1146 | 1.1118 | 1.1092 | 1.1067 | 1.1045
CS |  | m/s | 87.5574 | 86.9486 | 86.2592 | 418.2368 | 418.3338 | 418.4319 | 418.5301 | 418.6288 | 418.7263 | 418.9217 | 419.8983 | 420.8726 | 421.8466 | 422.8179 | 425.2383 | 427.6478 | 437.1775 | 446.5446 | 455.7644 | 464.847
T | 15 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.132 | 1.329 | 2.68 | 1622.682 | 1622.753 | 1622.824 | 1622.895 | 1622.966 | 1623.037 | 1623.179 | 1623.887 | 1624.591 | 1625.292 | 1625.99 | 1627.721 | 1629.434 | 1636.102 | 1642.498 | 1648.643 | 1654.555
V |  | kg/m3 | 7.5746 | 0.75218 | 0.37312 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000616 | 0.000615 | 0.000615 | 0.000614 | 0.000614 | 0.000611 | 0.000609 | 0.000607 | 0.000604
Z |  |  | 0.99923 | 0.99226 | 0.98443 | 0.002356 | 0.003141 | 0.003926 | 0.004711 | 0.005495 | 0.00628 | 0.00785 | 0.015693 | 0.02353 | 0.031361 | 0.039185 | 0.058719 | 0.078216 | 0.15584 | 0.23292 | 0.30951 | 0.38562
H |  | kJ/kg | 157.569 | 157.417 | 157.247 | 59.842 | 59.845 | 59.848 | 59.851 | 59.854 | 59.857 | 59.863 | 59.894 | 59.925 | 59.956 | 59.987 | 60.065 | 60.144 | 60.464 | 60.793 | 61.13 | 61.474
S |  | kJ/kg*K | 0.6547 | 0.5938 | 0.5752 | 0.2303 | 0.2303 | 0.2303 | 0.2302 | 0.2302 | 0.2302 | 0.2302 | 0.2301 | 0.23 | 0.2299 | 0.2298 | 0.2296 | 0.2293 | 0.2284 | 0.2275 | 0.2266 | 0.2258
CP |  | kJ/kg*K | 0.8833 | 0.8841 | 0.8851 | 1.1004 | 1.1004 | 1.1003 | 1.1003 | 1.1003 | 1.1002 | 1.1002 | 1.0999 | 1.0996 | 1.0993 | 1.099 | 1.0983 | 1.0976 | 1.095 | 1.0926 | 1.0904 | 1.0884
CP/CV |  |  | 1.0308 | 1.0316 | 1.0325 | 1.121 | 1.121 | 1.121 | 1.1209 | 1.1209 | 1.1209 | 1.1208 | 1.1204 | 1.1201 | 1.1198 | 1.1194 | 1.1186 | 1.1178 | 1.1147 | 1.1119 | 1.1092 | 1.1068
CS |  | m/s | 88.3278 | 87.7442 | 87.0842 | 403.6312 | 403.7301 | 403.8292 | 403.9288 | 404.0278 | 404.1269 | 404.3254 | 405.3158 | 406.3044 | 407.2899 | 408.2743 | 410.7249 | 413.1641 | 422.8019 | 432.2652 | 441.5676 | 450.72
T | 20 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.13 | 1.306 | 2.632 | 3.979 | 1607.98 | 1608.055 | 1608.131 | 1608.206 | 1608.282 | 1608.432 | 1609.184 | 1609.932 | 1610.676 | 1611.417 | 1613.254 | 1615.071 | 1622.135 | 1628.9 | 1635.388 | 1641.622
V |  | kg/m3 | 7.7063 | 0.76552 | 0.37989 | 0.25132 | 0.000622 | 0.000622 | 0.000622 | 0.000622 | 0.000622 | 0.000622 | 0.000621 | 0.000621 | 0.000621 | 0.000621 | 0.00062 | 0.000619 | 0.000616 | 0.000614 | 0.000611 | 0.000609
Z |  |  | 0.99927 | 0.99264 | 0.98519 | 0.97765 | 0.003114 | 0.003892 | 0.00467 | 0.005448 | 0.006226 | 0.007782 | 0.015558 | 0.023326 | 0.031088 | 0.038843 | 0.058202 | 0.077521 | 0.15441 | 0.23072 | 0.30649 | 0.38177
H |  | kJ/kg | 161.99 | 161.843 | 161.677 | 161.509 | 65.356 | 65.358 | 65.361 | 65.364 | 65.367 | 65.373 | 65.402 | 65.432 | 65.461 | 65.491 | 65.565 | 65.64 | 65.947 | 66.263 | 66.589 | 66.922
S |  | kJ/kg*K | 0.6699 | 0.609 | 0.5904 | 0.5794 | 0.2492 | 0.2492 | 0.2492 | 0.2492 | 0.2492 | 0.2492 | 0.2491 | 0.249 | 0.2488 | 0.2487 | 0.2485 | 0.2482 | 0.2472 | 0.2463 | 0.2454 | 0.2445
CP |  | kJ/kg*K | 0.8851 | 0.8859 | 0.8869 | 0.8878 | 1.104 | 1.1039 | 1.1039 | 1.1039 | 1.1039 | 1.1038 | 1.1035 | 1.1031 | 1.1028 | 1.1025 | 1.1017 | 1.101 | 1.0981 | 1.0955 | 1.0931 | 1.0909
CP/CV |  |  | 1.0307 | 1.0315 | 1.0324 | 1.0333 | 1.1246 | 1.1246 | 1.1246 | 1.1245 | 1.1245 | 1.1244 | 1.124 | 1.1236 | 1.1233 | 1.1229 | 1.122 | 1.1211 | 1.1177 | 1.1147 | 1.1118 | 1.1092
CS |  | m/s | 89.0912 | 88.5315 | 87.8992 | 87.2553 | 389.4693 | 389.5701 | 389.671 | 389.7714 | 389.8718 | 390.0729 | 391.077 | 392.0799 | 393.0801 | 394.0783 | 396.5629 | 399.0343 | 408.7924 | 418.3592 | 427.7515 | 436.9827
T | 25 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.128 | 1.284 | 2.586 | 3.908 | 5.249 | 1592.979 | 1593.059 | 1593.139 | 1593.219 | 1593.379 | 1594.178 | 1594.972 | 1595.763 | 1596.55 | 1598.5 | 1600.427 | 1607.912 | 1615.065 | 1621.915 | 1628.486
V |  | kg/m3 | 7.838 | 0.77885 | 0.38665 | 0.25589 | 0.19049 | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000627 | 0.000627 | 0.000627 | 0.000626 | 0.000626 | 0.000625 | 0.000622 | 0.000619 | 0.000617 | 0.000614
Z |  |  | 0.9993 | 0.99299 | 0.98591 | 0.97874 | 0.97148 | 0.003861 | 0.004633 | 0.005405 | 0.006177 | 0.007721 | 0.015434 | 0.02314 | 0.030839 | 0.03853 | 0.057728 | 0.076882 | 0.15308 | 0.22866 | 0.30368 | 0.37817
H |  | kJ/kg | 166.421 | 166.277 | 166.116 | 165.952 | 165.787 | 70.888 | 70.891 | 70.893 | 70.896 | 70.902 | 70.929 | 70.957 | 70.985 | 71.012 | 71.083 | 71.154 | 71.446 | 71.749 | 72.061 | 72.383
S |  | kJ/kg*K | 0.6849 | 0.624 | 0.6054 | 0.5944 | 0.5865 | 0.2679 | 0.2679 | 0.2679 | 0.2679 | 0.2679 | 0.2678 | 0.2676 | 0.2675 | 0.2674 | 0.2672 | 0.2669 | 0.2658 | 0.2649 | 0.2639 | 0.263
CP |  | kJ/kg*K | 0.8871 | 0.8879 | 0.8887 | 0.8897 | 0.8906 | 1.1079 | 1.1079 | 1.1079 | 1.1078 | 1.1078 | 1.1074 | 1.107 | 1.1067 | 1.1063 | 1.1055 | 1.1046 | 1.1015 | 1.0987 | 1.0961 | 1.0937
CP/CV |  |  | 1.0306 | 1.0314 | 1.0322 | 1.0331 | 1.0341 | 1.1284 | 1.1284 | 1.1283 | 1.1283 | 1.1282 | 1.1278 | 1.1274 | 1.127 | 1.1266 | 1.1256 | 1.1246 | 1.1209 | 1.1176 | 1.1145 | 1.1117
CS |  | m/s | 89.8477 | 89.3107 | 88.7046 | 88.0881 | 87.4607 | 375.6319 | 375.7344 | 375.8365 | 375.9389 | 376.1437 | 377.1638 | 378.1823 | 379.1984 | 380.2111 | 382.7336 | 385.2409 | 395.13 | 404.8092 | 414.3001 | 423.6164
T | 30 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.125 | 1.262 | 2.542 | 3.839 | 5.156 | 1577.588 | 1577.673 | 1577.758 | 1577.843 | 1578.014 | 1578.863 | 1579.707 | 1580.547 | 1581.383 | 1583.454 | 1585.498 | 1593.43 | 1600.995 | 1608.226 | 1615.151
V |  | kg/m3 | 7.9697 | 0.79218 | 0.3934 | 0.26045 | 0.19396 | 0.000634 | 0.000634 | 0.000634 | 0.000634 | 0.000634 | 0.000633 | 0.000633 | 0.000633 | 0.000632 | 0.000632 | 0.000631 | 0.000628 | 0.000625 | 0.000622 | 0.000619
Z |  |  | 0.99934 | 0.99333 | 0.98658 | 0.97976 | 0.97286 | 0.003834 | 0.0046 | 0.005366 | 0.006133 | 0.007665 | 0.015322 | 0.022971 | 0.030612 | 0.038245 | 0.057295 | 0.076298 | 0.15186 | 0.22676 | 0.30106 | 0.3748
H |  | kJ/kg | 170.861 | 170.721 | 170.564 | 170.405 | 170.245 | 76.438 | 76.441 | 76.443 | 76.446 | 76.451 | 76.477 | 76.502 | 76.528 | 76.554 | 76.62 | 76.687 | 76.962 | 77.25 | 77.55 | 77.859
S |  | kJ/kg*K | 0.6997 | 0.6388 | 0.6202 | 0.6092 | 0.6013 | 0.2864 | 0.2864 | 0.2864 | 0.2863 | 0.2863 | 0.2862 | 0.2861 | 0.286 | 0.2859 | 0.2856 | 0.2853 | 0.2842 | 0.2832 | 0.2822 | 0.2812
CP |  | kJ/kg*K | 0.8892 | 0.8899 | 0.8908 | 0.8917 | 0.8926 | 1.1123 | 1.1123 | 1.1122 | 1.1122 | 1.1121 | 1.1117 | 1.1113 | 1.1109 | 1.1105 | 1.1096 | 1.1087 | 1.1052 | 1.1021 | 1.0993 | 1.0967
CP/CV |  |  | 1.0306 | 1.0313 | 1.0321 | 1.0329 | 1.0338 | 1.1325 | 1.1324 | 1.1324 | 1.1323 | 1.1322 | 1.1318 | 1.1313 | 1.1309 | 1.1304 | 1.1293 | 1.1283 | 1.1242 | 1.1206 | 1.1173 | 1.1142
CS |  | m/s | 90.5975 | 90.082 | 89.5007 | 88.9101 | 88.3097 | 361.998 | 362.1019 | 362.2062 | 362.3102 | 362.5175 | 363.5561 | 364.5918 | 365.6245 | 366.6544 | 369.2177 | 371.7645 | 381.7972 | 391.601 | 401.1972 | 410.6065
T | 35 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.123 | 1.241 | 2.499 | 3.773 | 5.065 | 6.375 | 7.703 | 1562.056 | 1562.147 | 1562.328 | 1563.231 | 1564.129 | 1565.022 | 1565.91 | 1568.11 | 1570.281 | 1578.689 | 1586.689 | 1594.322 | 1601.619
V |  | kg/m3 | 8.1014 | 0.8055 | 0.40015 | 0.26501 | 0.19743 | 0.15687 | 0.12982 | 0.00064 | 0.00064 | 0.00064 | 0.00064 | 0.000639 | 0.000639 | 0.000639 | 0.000638 | 0.000637 | 0.000633 | 0.00063 | 0.000627 | 0.000624
Z |  |  | 0.99937 | 0.99364 | 0.98721 | 0.98072 | 0.97416 | 0.96752 | 0.96081 | 0.005332 | 0.006093 | 0.007615 | 0.015222 | 0.022819 | 0.030409 | 0.03799 | 0.056905 | 0.07577 | 0.15075 | 0.22502 | 0.29864 | 0.37167
H |  | kJ/kg | 175.313 | 175.177 | 175.024 | 174.869 | 174.713 | 174.554 | 174.394 | 82.016 | 82.019 | 82.023 | 82.047 | 82.07 | 82.094 | 82.118 | 82.179 | 82.241 | 82.498 | 82.77 | 83.055 | 83.351
S |  | kJ/kg*K | 0.7142 | 0.6534 | 0.6348 | 0.6238 | 0.6159 | 0.6097 | 0.6045 | 0.3046 | 0.3046 | 0.3046 | 0.3044 | 0.3043 | 0.3042 | 0.3041 | 0.3038 | 0.3035 | 0.3023 | 0.3012 | 0.3002 | 0.2992
CP |  | kJ/kg*K | 0.8914 | 0.8921 | 0.893 | 0.8938 | 0.8947 | 0.8956 | 0.8966 | 1.117 | 1.1169 | 1.1168 | 1.1164 | 1.116 | 1.1155 | 1.1151 | 1.114 | 1.113 | 1.1092 | 1.1058 | 1.1028 | 1.1
CP/CV |  |  | 1.0305 | 1.0312 | 1.0319 | 1.0328 | 1.0336 | 1.0345 | 1.0354 | 1.1367 | 1.1366 | 1.1365 | 1.136 | 1.1355 | 1.135 | 1.1345 | 1.1333 | 1.1321 | 1.1277 | 1.1237 | 1.1201 | 1.1168
CS |  | m/s | 91.3407 | 90.8457 | 90.288 | 89.7218 | 89.1468 | 88.5626 | 87.9689 | 348.8595 | 348.9655 | 349.1773 | 350.2352 | 351.2897 | 352.3408 | 353.3899 | 355.998 | 358.5882 | 368.7777 | 378.7159 | 388.4293 | 397.9382
T | 40 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.121 | 1.221 | 2.458 | 3.71 | 4.978 | 6.263 | 7.566 | 8.886 | 1546.25 | 1546.443 | 1547.404 | 1548.359 | 1549.308 | 1550.252 | 1552.589 | 1554.894 | 1563.804 | 1572.262 | 1580.314 | 1587.999
V |  | kg/m3 | 8.2331 | 0.81881 | 0.40688 | 0.26956 | 0.20088 | 0.15967 | 0.13218 | 0.11254 | 0.000647 | 0.000647 | 0.000646 | 0.000646 | 0.000645 | 0.000645 | 0.000644 | 0.000643 | 0.000639 | 0.000636 | 0.000633 | 0.00063
Z |  |  | 0.9994 | 0.99393 | 0.98781 | 0.98162 | 0.97537 | 0.96906 | 0.96268 | 0.95623 | 0.006057 | 0.007571 | 0.015132 | 0.022684 | 0.030226 | 0.03776 | 0.056554 | 0.075293 | 0.14973 | 0.2234 | 0.29639 | 0.36875
H |  | kJ/kg | 179.776 | 179.644 | 179.496 | 179.347 | 179.196 | 179.043 | 178.888 | 178.732 | 88.442 | 88.446 | 88.468 | 88.49 | 88.512 | 88.534 | 88.59 | 88.648 | 88.889 | 89.147 | 89.419 | 89.704
S |  | kJ/kg*K | 0.7286 | 0.6678 | 0.6492 | 0.6382 | 0.6303 | 0.6241 | 0.619 | 0.6146 | 0.3253 | 0.3252 | 0.3251 | 0.325 | 0.3249 | 0.3247 | 0.3244 | 0.3241 | 0.3229 | 0.3218 | 0.3207 | 0.3196
CP |  | kJ/kg*K | 0.8938 | 0.8945 | 0.8952 | 0.896 | 0.8968 | 0.8977 | 0.8986 | 0.8995 | 1.1037 | 1.1036 | 1.1031 | 1.1026 | 1.1021 | 1.1016 | 1.1005 | 1.0994 | 1.0953 | 1.0916 | 1.0882 | 1.0852
CP/CV |  |  | 1.0304 | 1.031 | 1.0318 | 1.0326 | 1.0333 | 1.0342 | 1.035 | 1.0359 | 1.1406 | 1.1404 | 1.1399 | 1.1393 | 1.1388 | 1.1382 | 1.1369 | 1.1356 | 1.1308 | 1.1265 | 1.1226 | 1.1191
CS |  | m/s | 92.0776 | 91.6016 | 91.0657 | 90.5222 | 89.9708 | 89.4111 | 88.8428 | 88.2656 | 335.9243 | 336.1409 | 337.2206 | 338.2968 | 339.3693 | 340.4384 | 343.0972 | 345.7361 | 356.1009 | 366.189 | 376.0306 | 385.651
T | 45 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.12 | 1.202 | 2.418 | 3.648 | 4.894 | 6.156 | 7.433 | 8.727 | 10.039 | 1530.254 | 1531.277 | 1532.294 | 1533.304 | 1534.308 | 1536.792 | 1539.24 | 1548.686 | 1557.63 | 1566.124 | 1574.214
V |  | kg/m3 | 8.3648 | 0.83212 | 0.41362 | 0.2741 | 0.20433 | 0.16246 | 0.13453 | 0.11458 | 0.09961 | 0.000653 | 0.000653 | 0.000653 | 0.000652 | 0.000652 | 0.000651 | 0.00065 | 0.000646 | 0.000642 | 0.000639 | 0.000635
Z |  |  | 0.99942 | 0.99421 | 0.98837 | 0.98247 | 0.97652 | 0.97051 | 0.96444 | 0.9583 | 0.95211 | 0.007532 | 0.015054 | 0.022565 | 0.030067 | 0.037558 | 0.056244 | 0.074871 | 0.14882 | 0.22194 | 0.29432 | 0.36604
H |  | kJ/kg | 184.251 | 184.123 | 183.979 | 183.833 | 183.686 | 183.537 | 183.387 | 183.235 | 183.081 | 93.979 | 93.998 | 94.017 | 94.036 | 94.056 | 94.106 | 94.158 | 94.378 | 94.616 | 94.871 | 95.14
S |  | kJ/kg*K | 0.7428 | 0.6819 | 0.6634 | 0.6524 | 0.6446 | 0.6384 | 0.6333 | 0.6289 | 0.625 | 0.3428 | 0.3426 | 0.3425 | 0.3424 | 0.3422 | 0.3419 | 0.3416 | 0.3403 | 0.3391 | 0.3379 | 0.3369
CP |  | kJ/kg*K | 0.8963 | 0.897 | 0.8977 | 0.8985 | 0.8992 | 0.9001 | 0.9009 | 0.9018 | 0.9027 | 1.1094 | 1.1088 | 1.1083 | 1.1078 | 1.1073 | 1.106 | 1.1047 | 1.1002 | 1.0961 | 1.0925 | 1.0892
CP/CV |  |  | 1.0303 | 1.0309 | 1.0316 | 1.0324 | 1.0331 | 1.0339 | 1.0347 | 1.0356 | 1.0365 | 1.1454 | 1.1448 | 1.1442 | 1.1436 | 1.1429 | 1.1415 | 1.14 | 1.1348 | 1.1301 | 1.1258 | 1.122
CS |  | m/s | 92.8082 | 92.3506 | 91.8359 | 91.3142 | 90.7853 | 90.249 | 89.705 | 89.153 | 88.5926 | 323.4868 | 324.5898 | 325.6885 | 326.7838 | 327.8752 | 330.5881 | 333.2778 | 343.8283 | 354.0739 | 364.0501 | 373.7839
T | 50 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.118 | 1.183 | 2.379 | 3.589 | 4.813 | 6.052 | 7.306 | 8.575 | 9.86 | 12.482 | 1514.8 | 1515.883 | 1516.959 | 1518.029 | 1520.672 | 1523.274 | 1533.295 | 1542.756 | 1551.719 | 1560.237
V |  | kg/m3 | 8.4965 | 0.84542 | 0.42034 | 0.27863 | 0.20777 | 0.16524 | 0.13688 | 0.11662 | 0.10142 | 0.080115 | 0.00066 | 0.00066 | 0.000659 | 0.000659 | 0.000658 | 0.000656 | 0.000652 | 0.000648 | 0.000644 | 0.000641
Z |  |  | 0.99945 | 0.99447 | 0.9889 | 0.98327 | 0.9776 | 0.97187 | 0.96609 | 0.96026 | 0.95436 | 0.9424 | 0.014988 | 0.022466 | 0.029932 | 0.037387 | 0.05598 | 0.074507 | 0.14801 | 0.22062 | 0.29245 | 0.36357
H |  | kJ/kg | 188.739 | 188.614 | 188.473 | 188.332 | 188.188 | 188.044 | 187.897 | 187.749 | 187.6 | 187.296 | 99.557 | 99.574 | 99.59 | 99.607 | 99.651 | 99.696 | 99.892 | 100.109 | 100.344 | 100.596
S |  | kJ/kg*K | 0.7568 | 0.696 | 0.6774 | 0.6665 | 0.6586 | 0.6524 | 0.6473 | 0.643 | 0.6391 | 0.6326 | 0.36 | 0.3598 | 0.3597 | 0.3595 | 0.3592 | 0.3588 | 0.3575 | 0.3562 | 0.355 | 0.3539
CP |  | kJ/kg*K | 0.899 | 0.8996 | 0.9003 | 0.901 | 0.9018 | 0.9026 | 0.9034 | 0.9042 | 0.905 | 0.9069 | 1.1151 | 1.1145 | 1.1139 | 1.1133 | 1.1119 | 1.1105 | 1.1054 | 1.101 | 1.097 | 1.0934
CP/CV |  |  | 1.0302 | 1.0308 | 1.0315 | 1.0322 | 1.0329 | 1.0337 | 1.0344 | 1.0353 | 1.0361 | 1.0379 | 1.15 | 1.1493 | 1.1487 | 1.148 | 1.1464 | 1.1448 | 1.1389 | 1.1337 | 1.1291 | 1.125
CS |  | m/s | 93.5328 | 93.0927 | 92.598 | 92.097 | 91.5896 | 91.0754 | 90.5543 | 90.0261 | 89.4903 | 88.3952 | 312.1753 | 313.2996 | 314.4203 | 315.5359 | 318.308 | 321.0547 | 331.8092 | 342.2261 | 352.3467 | 362.2057
T | 55 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1
r |  | kg/m3 | 0.116 | 1.165 | 2.342 | 3.532 | 4.735 | 5.952 | 7.183 | 8.428 | 9.689 | 12.257 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
V |  | kg/m3 | 8.6282 | 0.85871 | 0.42706 | 0.28316 | 0.2112 | 0.16802 | 0.13922 | 0.11865 | 0.10321 | 0.081589 | 1497.956 | 1499.112 | 1500.259 | 1501.399 | 1504.215 | 1506.984 | 1517.625 | 1527.638 | 1537.098 | 1546.066
Z |  |  | 0.99947 | 0.99472 | 0.9894 | 0.98403 | 0.97862 | 0.97316 | 0.96765 | 0.9621 | 0.95649 | 0.94511 | 0.000668 | 0.000667 | 0.000667 | 0.000666 | 0.000665 | 0.000664 | 0.000659 | 0.000655 | 0.000651 | 0.000647
H |  | kJ/kg | 193.241 | 193.119 | 192.982 | 192.843 | 192.704 | 192.563 | 192.421 | 192.277 | 192.131 | 191.836 | 0.014936 | 0.022385 | 0.029822 | 0.037248 | 0.055761 | 0.074203 | 0.14731 | 0.21946 | 0.29077 | 0.36132
S |  | kJ/kg*K | 0.7706 | 0.7098 | 0.6913 | 0.6803 | 0.6725 | 0.6663 | 0.6612 | 0.6569 | 0.6531 | 0.6466 | 105.15 | 105.163 | 105.177 | 105.19 | 105.226 | 105.264 | 105.433 | 105.626 | 105.841 | 106.074
CP |  | kJ/kg*K | 0.9017 | 0.9023 | 0.903 | 0.9037 | 0.9045 | 0.9052 | 0.906 | 0.9068 | 0.9076 | 0.9093 | 0.3771 | 0.377 | 0.3768 | 0.3767 | 0.3763 | 0.3759 | 0.3745 | 0.3732 | 0.3719 | 0.3707
CP/CV |  |  | 1.0301 | 1.0307 | 1.0313 | 1.032 | 1.0327 | 1.0334 | 1.0342 | 1.0349 | 1.0357 | 1.0374 | 1.122 | 1.1213 | 1.1206 | 1.1199 | 1.1183 | 1.1168 | 1.1111 | 1.1062 | 1.1018 | 1.0979
CS |  | m/s | 94.2515 | 93.8281 | 93.3524 | 92.8711 | 92.384 | 91.8908 | 91.3914 | 90.8855 | 90.3729 | 89.3267 | 1.1557 | 1.1549 | 1.1542 | 1.1534 | 1.1516 | 1.1498 | 1.1433 | 1.1376 | 1.1326 | 1.1281
[13 empty] | 299.9596 | 301.1122 | 302.2605 | 303.4037 | 306.2415 | 309.051 | 320.0289 | 330.6329 | 340.9113 | 350.903
T | 60 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.114 | 1.147 | 2.305 | 3.476 | 4.659 | 5.855 | 7.064 | 8.287 | 9.523 | 12.04 | 1480.723 | 1481.958 | 1483.185 | 1484.402 | 1487.406 | 1490.357 | 1501.667 | 1512.271 | 1522.26 | 1531.705
V |  | kg/m3 | 8.7599 | 0.872 | 0.43377 | 0.28769 | 0.21463 | 0.17079 | 0.14156 | 0.12068 | 0.10501 | 0.083056 | 0.000675 | 0.000675 | 0.000674 | 0.000674 | 0.000672 | 0.000671 | 0.000666 | 0.000661 | 0.000657 | 0.000653
Z |  |  | 0.9995 | 0.99495 | 0.98987 | 0.98475 | 0.97958 | 0.97437 | 0.96912 | 0.96383 | 0.95849 | 0.94767 | 0.014897 | 0.022325 | 0.02974 | 0.037141 | 0.05559 | 0.073961 | 0.14673 | 0.21846 | 0.28928 | 0.3593
H |  | kJ/kg | 197.757 | 197.638 | 197.504 | 197.369 | 197.233 | 197.096 | 196.957 | 196.817 | 196.676 | 196.389 | 110.778 | 110.788 | 110.797 | 110.808 | 110.835 | 110.865 | 111.003 | 111.171 | 111.363 | 111.576
S |  | kJ/kg*K | 0.7843 | 0.7235 | 0.7049 | 0.694 | 0.6862 | 0.68 | 0.6749 | 0.6706 | 0.6668 | 0.6603 | 0.3942 | 0.394 | 0.3938 | 0.3937 | 0.3933 | 0.3929 | 0.3913 | 0.3899 | 0.3886 | 0.3873
CP |  | kJ/kg*K | 0.9046 | 0.9052 | 0.9059 | 0.9066 | 0.9073 | 0.908 | 0.9087 | 0.9095 | 0.9103 | 0.9119 | 1.1294 | 1.1286 | 1.1279 | 1.1271 | 1.1253 | 1.1235 | 1.1172 | 1.1117 | 1.1069 | 1.1027
CP/CV |  |  | 1.03 | 1.0306 | 1.0312 | 1.0318 | 1.0325 | 1.0332 | 1.0339 | 1.0346 | 1.0354 | 1.037 | 1.1619 | 1.161 | 1.1601 | 1.1593 | 1.1572 | 1.1552 | 1.148 | 1.1417 | 1.1362 | 1.1313
CS |  | m/s | 94.9643 | 94.5569 | 94.0994 | 93.6368 | 93.169 | 92.6956 | 92.2167 | 91.732 | 91.2412 | 90.2409 | 287.9234 | 289.1082 | 290.2869 | 291.4606 | 294.3715 | 297.2507 | 308.4744 | 319.2824 | 329.7314 | 339.8665
T | 65 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.112 | 1.13 | 2.27 | 3.422 | 4.586 | 5.762 | 6.95 | 8.15 | 9.364 | 11.832 | 1463.076 | 1464.399 | 1465.712 | 1467.014 | 1470.225 | 1473.375 | 1485.412 | 1496.652 | 1507.204 | 1517.153
V |  | kg/m3 | 8.8915 | 0.88529 | 0.44048 | 0.2922 | 0.21806 | 0.17356 | 0.14389 | 0.12269 | 0.10679 | 0.084517 | 0.000683 | 0.000683 | 0.000682 | 0.000682 | 0.00068 | 0.000679 | 0.000673 | 0.000668 | 0.000663 | 0.000659
Z |  |  | 0.99952 | 0.99518 | 0.99032 | 0.98542 | 0.98049 | 0.97552 | 0.97052 | 0.96547 | 0.96038 | 0.95008 | 0.014872 | 0.022286 | 0.029685 | 0.037069 | 0.055469 | 0.073784 | 0.14626 | 0.21761 | 0.28799 | 0.35751
H |  | kJ/kg | 202.288 | 202.171 | 202.041 | 201.909 | 201.777 | 201.643 | 201.508 | 201.372 | 201.234 | 200.955 | 116.445 | 116.451 | 116.456 | 116.463 | 116.48 | 116.5 | 116.605 | 116.744 | 116.911 | 117.102
S |  | kJ/kg*K | 0.7978 | 0.737 | 0.7185 | 0.7075 | 0.6997 | 0.6936 | 0.6885 | 0.6842 | 0.6804 | 0.674 | 0.4111 | 0.4109 | 0.4107 | 0.4105 | 0.4101 | 0.4097 | 0.408 | 0.4065 | 0.4051 | 0.4038
CP |  | kJ/kg*K | 0.9077 | 0.9082 | 0.9089 | 0.9095 | 0.9102 | 0.9109 | 0.9116 | 0.9123 | 0.9131 | 0.9146 | 1.1376 | 1.1367 | 1.1358 | 1.1349 | 1.1329 | 1.1309 | 1.1237 | 1.1176 | 1.1124 | 1.1077
CP/CV |  |  | 1.0299 | 1.0304 | 1.031 | 1.0316 | 1.0323 | 1.0329 | 1.0336 | 1.0343 | 1.035 | 1.0365 | 1.1686 | 1.1676 | 1.1666 | 1.1657 | 1.1633 | 1.1611 | 1.153 | 1.146 | 1.14 | 1.1346
CS |  | m/s | 95.6715 | 95.2793 | 94.8391 | 94.3944 | 93.9448 | 93.4904 | 93.0309 | 92.5661 | 92.096 | 91.1388 | 276.0467 | 277.2665 | 278.4805 | 279.6878 | 282.6803 | 285.6367 | 297.1327 | 308.1634 | 318.7971 | 329.0869
T | 70 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.111 | 1.113 | 2.236 | 3.37 | 4.515 | 5.671 | 6.839 | 8.019 | 9.21 | 11.632 | 1444.983 | 1446.403 | 1447.812 | 1449.208 | 1452.648 | 1456.016 | 1468.848 | 1480.773 | 1491.927 | 1502.412
V |  | kg/m3 | 9.0232 | 0.89857 | 0.44719 | 0.29672 | 0.22148 | 0.17632 | 0.14622 | 0.12471 | 0.10857 | 0.085972 | 0.000692 | 0.000691 | 0.000691 | 0.00069 | 0.000688 | 0.000687 | 0.000681 | 0.000675 | 0.00067 | 0.000666
Z |  |  | 0.99954 | 0.99539 | 0.99074 | 0.98606 | 0.98135 | 0.97661 | 0.97183 | 0.96701 | 0.96216 | 0.95235 | 0.014863 | 0.02227 | 0.02966 | 0.037034 | 0.055402 | 0.073676 | 0.14591 | 0.21693 | 0.2869 | 0.35594
H |  | kJ/kg | 206.834 | 206.72 | 206.593 | 206.465 | 206.335 | 206.205 | 206.073 | 205.941 | 205.807 | 205.536 | 122.155 | 122.155 | 122.157 | 122.158 | 122.165 | 122.174 | 122.241 | 122.348 | 122.487 | 122.653
S |  | kJ/kg*K | 0.8111 | 0.7503 | 0.7318 | 0.7209 | 0.7131 | 0.707 | 0.7019 | 0.6976 | 0.6938 | 0.6874 | 0.4278 | 0.4276 | 0.4274 | 0.4272 | 0.4268 | 0.4263 | 0.4246 | 0.423 | 0.4215 | 0.4201
CP |  | kJ/kg*K | 0.9108 | 0.9114 | 0.912 | 0.9126 | 0.9132 | 0.9139 | 0.9146 | 0.9153 | 0.916 | 0.9175 | 1.1465 | 1.1455 | 1.1445 | 1.1435 | 1.1411 | 1.1388 | 1.1308 | 1.124 | 1.1181 | 1.113
CP/CV |  |  | 1.0298 | 1.0303 | 1.0309 | 1.0315 | 1.0321 | 1.0327 | 1.0334 | 1.034 | 1.0347 | 1.0361 | 1.176 | 1.1748 | 1.1737 | 1.1726 | 1.17 | 1.1674 | 1.1583 | 1.1506 | 1.1439 | 1.1381
CS |  | m/s | 96.3732 | 95.9954 | 95.5719 | 95.1441 | 94.712 | 94.2754 | 93.8343 | 93.3885 | 92.9378 | 92.0214 | 264.308 | 265.5679 | 266.8207 | 268.0662 | 271.1498 | 274.1926 | 285.9888 | 297.2638 | 308.0983 | 318.5542
T | 75 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.109 | 1.097 | 2.203 | 3.32 | 4.447 | 5.584 | 6.732 | 7.892 | 9.062 | 11.439 | 24.118 | 1427.932 | 1429.448 | 1430.949 | 1434.643 | 1438.255 | 1451.958 | 1464.627 | 1476.426 | 1487.48
V |  | kg/m3 | 9.1548 | 0.91184 | 0.45389 | 0.30123 | 0.22489 | 0.17908 | 0.14854 | 0.12672 | 0.11035 | 0.087421 | 0.041463 | 0.0007 | 0.0007 | 0.000699 | 0.000697 | 0.000695 | 0.000689 | 0.000683 | 0.000677 | 0.000672
Z |  |  | 0.99956 | 0.99559 | 0.99114 | 0.98667 | 0.98217 | 0.97764 | 0.97307 | 0.96848 | 0.96385 | 0.95449 | 0.90541 | 0.022278 | 0.029667 | 0.037039 | 0.055392 | 0.073642 | 0.14569 | 0.21642 | 0.28601 | 0.35461
H |  | kJ/kg | 211.396 | 211.285 | 211.161 | 211.035 | 210.909 | 210.782 | 210.654 | 210.525 | 210.395 | 210.131 | 208.738 | 127.907 | 127.902 | 127.899 | 127.892 | 127.89 | 127.914 | 127.984 | 128.092 | 128.233
S |  | kJ/kg*K | 0.8243 | 0.7635 | 0.745 | 0.7341 | 0.7263 | 0.7202 | 0.7152 | 0.7108 | 0.7071 | 0.7007 | 0.6797 | 0.4443 | 0.444 | 0.4438 | 0.4433 | 0.4428 | 0.441 | 0.4393 | 0.4377 | 0.4362
CP |  | kJ/kg*K | 0.9141 | 0.9146 | 0.9152 | 0.9158 | 0.9164 | 0.9171 | 0.9177 | 0.9184 | 0.9191 | 0.9205 | 0.929 | 1.1551 | 1.154 | 1.1528 | 1.1501 | 1.1475 | 1.1383 | 1.1307 | 1.1242 | 1.1187
CP/CV |  |  | 1.0297 | 1.0302 | 1.0307 | 1.0313 | 1.0319 | 1.0325 | 1.0331 | 1.0337 | 1.0344 | 1.0357 | 1.044 | 1.1828 | 1.1815 | 1.1803 | 1.1772 | 1.1743 | 1.164 | 1.1554 | 1.1481 | 1.1417
CS |  | m/s | 97.0694 | 96.7056 | 96.2978 | 95.8862 | 95.4707 | 95.0511 | 94.6275 | 94.1996 | 93.7674 | 92.8893 | 88.1885 | 253.9889 | 255.2854 | 256.5742 | 259.7609 | 262.9 | 275.0309 | 286.5735 | 297.6254 | 308.2607
T | 80 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.108 | 1.081 | 2.171 | 3.271 | 4.38 | 5.5 | 6.629 | 7.769 | 8.919 | 11.253 | 23.66 | 1408.935 | 1410.572 | 1412.193 | 1416.172 | 1420.056 | 1434.723 | 1448.202 | 1460.696 | 1472.356
V |  | kg/m3 | 9.2865 | 0.92512 | 0.46058 | 0.30573 | 0.2283 | 0.18183 | 0.15085 | 0.12872 | 0.11212 | 0.088865 | 0.042265 | 0.00071 | 0.000709 | 0.000708 | 0.000706 | 0.000704 | 0.000697 | 0.000691 | 0.000685 | 0.000679
Z |  |  | 0.99958 | 0.99577 | 0.99152 | 0.98725 | 0.98294 | 0.97861 | 0.97425 | 0.96986 | 0.96545 | 0.95652 | 0.90985 | 0.022314 | 0.02971 | 0.037087 | 0.055444 | 0.073686 | 0.14561 | 0.21608 | 0.28533 | 0.35352
H |  | kJ/kg | 215.975 | 215.866 | 215.745 | 215.623 | 215.5 | 215.376 | 215.251 | 215.125 | 214.998 | 214.741 | 213.39 | 133.708 | 133.698 | 133.688 | 133.667 | 133.651 | 133.626 | 133.655 | 133.73 | 133.841
S |  | kJ/kg*K | 0.8374 | 0.7766 | 0.7581 | 0.7472 | 0.7394 | 0.7333 | 0.7283 | 0.724 | 0.7202 | 0.7138 | 0.6929 | 0.4608 | 0.4606 | 0.4604 | 0.4598 | 0.4593 | 0.4573 | 0.4555 | 0.4538 | 0.4522
CP |  | kJ/kg*K | 0.9175 | 0.918 | 0.9185 | 0.9191 | 0.9197 | 0.9203 | 0.921 | 0.9216 | 0.9223 | 0.9236 | 0.9317 | 1.1658 | 1.1644 | 1.1631 | 1.1599 | 1.157 | 1.1465 | 1.1379 | 1.1307 | 1.1246
CP/CV |  |  | 1.0296 | 1.03 | 1.0306 | 1.0311 | 1.0317 | 1.0322 | 1.0328 | 1.0334 | 1.0341 | 1.0354 | 1.0431 | 1.1917 | 1.1902 | 1.1888 | 1.1852 | 1.1819 | 1.1702 | 1.1606 | 1.1525 | 1.1455
CS |  | m/s | 97.7604 | 97.4098 | 97.0171 | 96.6209 | 96.2212 | 95.8179 | 95.4109 | 95 | 94.5852 | 93.7435 | 89.2583 | 242.5044 | 243.8515 | 245.1889 | 248.4921 | 251.7406 | 264.2444 | 276.0812 | 287.3695 | 298.1979
T | 85 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.106 | 1.066 | 2.14 | 3.223 | 4.316 | 5.418 | 6.529 | 7.65 | 8.781 | 11.074 | 23.223 | 36.77 | 1391.125 | 1392.881 | 1397.187 | 1401.377 | 1417.119 | 1431.486 | 1444.731 | 1457.04
V |  | kg/m3 | 9.4181 | 0.93838 | 0.46727 | 0.31023 | 0.2317 | 0.18458 | 0.15316 | 0.13072 | 0.11388 | 0.090304 | 0.04306 | 0.027196 | 0.000719 | 0.000718 | 0.000716 | 0.000714 | 0.000706 | 0.000699 | 0.000692 | 0.000686
Z |  |  | 0.9996 | 0.99595 | 0.99189 | 0.98779 | 0.98368 | 0.97954 | 0.97537 | 0.97118 | 0.96696 | 0.95844 | 0.91404 | 0.86594 | 0.029792 | 0.037183 | 0.055565 | 0.073817 | 0.14567 | 0.21593 | 0.28487 | 0.35267
H |  | kJ/kg | 220.571 | 220.465 | 220.346 | 220.227 | 220.107 | 219.986 | 219.864 | 219.741 | 219.617 | 219.367 | 218.055 | 216.618 | 139.549 | 139.532 | 139.494 | 139.461 | 139.38 | 139.364 | 139.4 | 139.479
S |  | kJ/kg*K | 0.8503 | 0.7895 | 0.7711 | 0.7602 | 0.7524 | 0.7463 | 0.7412 | 0.7369 | 0.7332 | 0.7268 | 0.7061 | 0.6925 | 0.477 | 0.4768 | 0.4762 | 0.4756 | 0.4735 | 0.4715 | 0.4697 | 0.4681
CP |  | kJ/kg*K | 0.921 | 0.9214 | 0.922 | 0.9226 | 0.9231 | 0.9237 | 0.9243 | 0.925 | 0.9256 | 0.9269 | 0.9346 | 0.9448 | 1.1761 | 1.1745 | 1.1708 | 1.1673 | 1.1553 | 1.1456 | 1.1376 | 1.1308
CP/CV |  |  | 1.0295 | 1.0299 | 1.0304 | 1.0309 | 1.0315 | 1.032 | 1.0326 | 1.0332 | 1.0338 | 1.035 | 1.0423 | 1.0524 | 1.2 | 1.1983 | 1.1942 | 1.1903 | 1.177 | 1.1661 | 1.1571 | 1.1494
CS |  | m/s | 98.4462 | 98.1083 | 97.73 | 97.3486 | 96.964 | 96.5761 | 96.1848 | 95.7901 | 95.3919 | 94.5845 | 90.3013 | 85.5052 | 232.4909 | 233.8845 | 237.3207 | 240.693 | 253.6149 | 265.7758 | 277.3218 | 288.3579
T | 90 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.105 | 1.051 | 2.11 | 3.177 | 4.253 | 5.338 | 6.432 | 7.535 | 8.647 | 10.901 | 22.805 | 35.993 | 1371.029 | 1372.942 | 1377.621 | 1382.162 | 1399.115 | 1414.462 | 1428.523 | 1441.527
V |  | kg/m3 | 9.5498 | 0.95165 | 0.47396 | 0.31473 | 0.23511 | 0.18733 | 0.15547 | 0.13271 | 0.11564 | 0.091738 | 0.043849 | 0.027783 | 0.000729 | 0.000728 | 0.000726 | 0.000724 | 0.000715 | 0.000707 | 0.0007 | 0.000694
Z |  |  | 0.99961 | 0.99613 | 0.99223 | 0.98831 | 0.98437 | 0.98041 | 0.97643 | 0.97242 | 0.96839 | 0.96026 | 0.91798 | 0.87245 | 0.029919 | 0.037333 | 0.055761 | 0.074044 | 0.14589 | 0.21598 | 0.28463 | 0.35208
H |  | kJ/kg | 225.185 | 225.081 | 224.965 | 224.849 | 224.731 | 224.613 | 224.494 | 224.375 | 224.254 | 224.01 | 222.736 | 221.347 | 145.461 | 145.436 | 145.377 | 145.326 | 145.18 | 145.112 | 145.106 | 145.149
S |  | kJ/kg*K | 0.8631 | 0.8023 | 0.7839 | 0.773 | 0.7652 | 0.7591 | 0.7541 | 0.7498 | 0.7461 | 0.7397 | 0.719 | 0.7056 | 0.4934 | 0.4932 | 0.4925 | 0.4919 | 0.4895 | 0.4874 | 0.4855 | 0.4838
CP |  | kJ/kg*K | 0.9246 | 0.925 | 0.9256 | 0.9261 | 0.9267 | 0.9272 | 0.9278 | 0.9284 | 0.929 | 0.9303 | 0.9376 | 0.9472 | 1.1891 | 1.1873 | 1.1829 | 1.1788 | 1.1648 | 1.1538 | 1.1448 | 1.1374
CP/CV |  |  | 1.0293 | 1.0298 | 1.0303 | 1.0308 | 1.0313 | 1.0318 | 1.0323 | 1.0329 | 1.0335 | 1.0346 | 1.0416 | 1.0509 | 1.211 | 1.209 | 1.2042 | 1.1997 | 1.1843 | 1.172 | 1.162 | 1.1536
CS |  | m/s | 99.1269 | 98.8012 | 98.4367 | 98.0693 | 97.6991 | 97.3259 | 96.9497 | 96.5703 | 96.1878 | 95.413 | 91.3192 | 86.7747 | 221.1721 | 222.6306 | 226.2203 | 229.734 | 243.1275 | 255.6476 | 267.4743 | 278.7343
T | 95 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.103 | 1.036 | 2.081 | 3.133 | 4.193 | 5.261 | 6.338 | 7.424 | 8.518 | 10.733 | 22.405 | 35.258 | 1350.179 | 1352.277 | 1357.394 | 1362.342 | 1380.673 | 1397.107 | 1412.06 | 1425.813
V |  | kg/m3 | 9.6814 | 0.96491 | 0.48065 | 0.31922 | 0.2385 | 0.19007 | 0.15777 | 0.1347 | 0.1174 | 0.093168 | 0.044633 | 0.028362 | 0.000741 | 0.000739 | 0.000737 | 0.000734 | 0.000724 | 0.000716 | 0.000708 | 0.000701
Z |  |  | 0.99963 | 0.99629 | 0.99256 | 0.98881 | 0.98503 | 0.98125 | 0.97743 | 0.9736 | 0.96975 | 0.96198 | 0.92169 | 0.87855 | 0.030095 | 0.037544 | 0.056043 | 0.074377 | 0.14627 | 0.21624 | 0.28464 | 0.35174
H |  | kJ/kg | 229.817 | 229.715 | 229.602 | 229.488 | 229.374 | 229.258 | 229.142 | 229.026 | 228.908 | 228.671 | 227.431 | 226.089 | 151.443 | 151.407 | 151.325 | 151.251 | 151.029 | 150.903 | 150.849 | 150.853
S |  | kJ/kg*K | 0.8758 | 0.815 | 0.7965 | 0.7857 | 0.7779 | 0.7718 | 0.7668 | 0.7625 | 0.7588 | 0.7525 | 0.7319 | 0.7186 | 0.5098 | 0.5095 | 0.5088 | 0.5081 | 0.5055 | 0.5033 | 0.5013 | 0.4994
CP |  | kJ/kg*K | 0.9283 | 0.9287 | 0.9292 | 0.9298 | 0.9303 | 0.9309 | 0.9314 | 0.932 | 0.9326 | 0.9338 | 0.9408 | 0.9497 | 1.2039 | 1.2017 | 1.1964 | 1.1915 | 1.1752 | 1.1626 | 1.1525 | 1.1442
CP/CV |  |  | 1.0292 | 1.0296 | 1.0301 | 1.0306 | 1.0311 | 1.0316 | 1.0321 | 1.0326 | 1.0332 | 1.0343 | 1.0408 | 1.0495 | 1.2237 | 1.2213 | 1.2155 | 1.2102 | 1.1923 | 1.1784 | 1.1672 | 1.1579
CS |  | m/s | 99.8026 | 99.4886 | 99.1373 | 98.7834 | 98.4269 | 98.0677 | 97.7058 | 97.3411 | 96.9735 | 96.2296 | 92.3138 | 88.0012 | 209.8576 | 211.3922 | 215.1607 | 218.8381 | 232.767 | 245.6857 | 257.8188 | 269.3205
T | 100 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.102 | 1.022 | 2.052 | 3.089 | 4.134 | 5.187 | 6.247 | 7.316 | 8.393 | 10.572 | 22.021 | 34.56 | 48.503 | 1330.757 | 1336.396 | 1341.822 | 1361.741 | 1379.397 | 1395.329 | 1409.893
V |  | kg/m3 | 9.8131 | 0.97816 | 0.48733 | 0.32371 | 0.24189 | 0.1928 | 0.16007 | 0.13669 | 0.11915 | 0.094593 | 0.045411 | 0.028935 | 0.020617 | 0.000751 | 0.000748 | 0.000745 | 0.000734 | 0.000725 | 0.000717 | 0.000709
Z |  |  | 0.99965 | 0.99644 | 0.99287 | 0.98927 | 0.98566 | 0.98203 | 0.97839 | 0.97472 | 0.97104 | 0.96361 | 0.9252 | 0.88427 | 0.8401 | 0.037826 | 0.056423 | 0.074832 | 0.14684 | 0.21672 | 0.28489 | 0.35168
H |  | kJ/kg | 234.467 | 234.368 | 234.258 | 234.146 | 234.035 | 233.922 | 233.809 | 233.695 | 233.58 | 233.349 | 232.143 | 230.845 | 229.426 | 157.456 | 157.344 | 157.243 | 156.933 | 156.739 | 156.632 | 156.592
S |  | kJ/kg*K | 0.8883 | 0.8275 | 0.8091 | 0.7982 | 0.7905 | 0.7844 | 0.7794 | 0.7751 | 0.7714 | 0.7651 | 0.7446 | 0.7314 | 0.7211 | 0.5258 | 0.525 | 0.5242 | 0.5215 | 0.519 | 0.5169 | 0.5149
CP |  | kJ/kg*K | 0.9321 | 0.9325 | 0.933 | 0.9335 | 0.9341 | 0.9346 | 0.9351 | 0.9357 | 0.9363 | 0.9374 | 0.9441 | 0.9525 | 0.9637 | 1.2181 | 1.2116 | 1.2057 | 1.1865 | 1.172 | 1.1606 | 1.1515
CP/CV |  |  | 1.0291 | 1.0295 | 1.0299 | 1.0304 | 1.0309 | 1.0314 | 1.0319 | 1.0324 | 1.0329 | 1.034 | 1.0402 | 1.0482 | 1.0591 | 1.2355 | 1.2286 | 1.2222 | 1.2012 | 1.1853 | 1.1727 | 1.1624
CS |  | m/s | 100.4736 | 100.1707 | 99.832 | 99.491 | 99.1476 | 98.8018 | 98.4535 | 98.1028 | 97.7494 | 97.0348 | 93.2866 | 89.1885 | 84.6291 | 200.1263 | 204.1057 | 207.974 | 222.5162 | 235.8795 | 248.3482 | 260.1102
T | 105 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.101 | 1.009 | 2.024 | 3.047 | 4.077 | 5.114 | 6.159 | 7.211 | 8.271 | 10.415 | 21.652 | 33.898 | 47.418 | 62.624 | 1314.479 | 1320.48 | 1342.258 | 1361.297 | 1378.312 | 1393.757
V |  | kg/m3 | 9.9447 | 0.99142 | 0.494 | 0.32819 | 0.24529 | 0.19554 | 0.16237 | 0.13867 | 0.1209 | 0.096015 | 0.046185 | 0.029501 | 0.021089 | 0.015968 | 0.000761 | 0.000757 | 0.000745 | 0.000735 | 0.000726 | 0.000717
Z |  |  | 0.99966 | 0.99659 | 0.99316 | 0.98972 | 0.98626 | 0.98279 | 0.9793 | 0.97579 | 0.97226 | 0.96516 | 0.92851 | 0.88964 | 0.84796 | 0.80258 | 0.056919 | 0.075428 | 0.14762 | 0.21744 | 0.28542 | 0.35189
H |  | kJ/kg | 239.138 | 239.041 | 238.933 | 238.824 | 238.714 | 238.604 | 238.494 | 238.383 | 238.271 | 238.045 | 236.872 | 235.615 | 234.25 | 232.743 | 163.445 | 163.311 | 162.896 | 162.624 | 162.456 | 162.368
S |  | kJ/kg*K | 0.9007 | 0.84 | 0.8216 | 0.8107 | 0.8029 | 0.7968 | 0.7919 | 0.7876 | 0.7839 | 0.7776 | 0.7572 | 0.7441 | 0.7339 | 0.7251 | 0.5412 | 0.5404 | 0.5373 | 0.5347 | 0.5324 | 0.5303
CP |  | kJ/kg*K | 0.936 | 0.9364 | 0.9369 | 0.9374 | 0.9379 | 0.9384 | 0.939 | 0.9395 | 0.94 | 0.9412 | 0.9475 | 0.9554 | 0.9658 | 0.9799 | 1.2291 | 1.2219 | 1.1989 | 1.1821 | 1.1693 | 1.159
CP/CV |  |  | 1.029 | 1.0293 | 1.0298 | 1.0302 | 1.0307 | 1.0312 | 1.0316 | 1.0321 | 1.0326 | 1.0336 | 1.0395 | 1.047 | 1.057 | 1.071 | 1.2438 | 1.236 | 1.211 | 1.1927 | 1.1786 | 1.1672
CS |  | m/s | 101.1397 | 100.8475 | 100.521 | 100.1923 | 99.8614 | 99.5284 | 99.1932 | 98.8557 | 98.5159 | 97.8291 | 94.2389 | 90.3399 | 86.0416 | 81.2018 | 193.0108 | 197.1054 | 212.3564 | 226.2183 | 239.0552 | 251.0988
T | 110 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.099 | 0.995 | 1.997 | 3.006 | 4.021 | 5.044 | 6.073 | 7.11 | 8.153 | 10.263 | 21.298 | 33.266 | 46.397 | 61.032 | 1291.441 | 1298.149 | 1322.142 | 1342.764 | 1360.987 | 1377.396
V |  | kg/m3 | 10.0763 | 1.0047 | 0.50068 | 0.33268 | 0.24867 | 0.19827 | 0.16466 | 0.14065 | 0.12265 | 0.097433 | 0.046953 | 0.030061 | 0.021553 | 0.016385 | 0.000774 | 0.00077 | 0.000756 | 0.000745 | 0.000735 | 0.000726
Z |  |  | 0.99967 | 0.99673 | 0.99344 | 0.99014 | 0.98683 | 0.9835 | 0.98016 | 0.9768 | 0.97343 | 0.96663 | 0.93165 | 0.8947 | 0.85531 | 0.81277 | 0.057552 | 0.076189 | 0.14864 | 0.21844 | 0.28623 | 0.35241
H |  | kJ/kg | 243.827 | 243.733 | 243.627 | 243.521 | 243.414 | 243.306 | 243.198 | 243.09 | 242.981 | 242.76 | 241.619 | 240.4 | 239.084 | 237.645 | 169.64 | 169.466 | 168.924 | 168.562 | 168.325 | 168.183
S |  | kJ/kg*K | 0.9131 | 0.8523 | 0.8339 | 0.823 | 0.8153 | 0.8092 | 0.8042 | 0.8 | 0.7962 | 0.79 | 0.7697 | 0.7567 | 0.7467 | 0.738 | 0.5575 | 0.5566 | 0.5532 | 0.5503 | 0.5478 | 0.5455
CP |  | kJ/kg*K | 0.94 | 0.9404 | 0.9409 | 0.9414 | 0.9419 | 0.9424 | 0.9429 | 0.9434 | 0.9439 | 0.945 | 0.9511 | 0.9586 | 0.9681 | 0.9809 | 1.2496 | 1.2405 | 1.2126 | 1.193 | 1.1784 | 1.167
CP/CV |  |  | 1.0288 | 1.0292 | 1.0296 | 1.0301 | 1.0305 | 1.0309 | 1.0314 | 1.0319 | 1.0323 | 1.0333 | 1.0389 | 1.0459 | 1.0551 | 1.0677 | 1.2618 | 1.2521 | 1.2221 | 1.2009 | 1.1849 | 1.1722
CS |  | m/s | 101.8012 | 101.5193 | 101.2043 | 100.8874 | 100.5686 | 100.2478 | 99.925 | 99.6002 | 99.2733 | 98.613 | 95.1721 | 91.4582 | 87.398 | 82.8797 | 181.8196 | 186.187 | 202.2673 | 216.6914 | 229.9335 | 242.2809
T | 115 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.098 | 0.982 | 1.971 | 2.966 | 3.967 | 4.975 | 5.99 | 7.011 | 8.039 | 10.117 | 20.957 | 32.664 | 45.434 | 59.554 | 1266.997 | 1274.599 | 1301.286 | 1323.746 | 1343.327 | 1360.796
V |  | kg/m3 | 10.208 | 1.0179 | 0.50735 | 0.33715 | 0.25205 | 0.20099 | 0.16695 | 0.14263 | 0.12439 | 0.098847 | 0.047717 | 0.030615 | 0.02201 | 0.016792 | 0.000789 | 0.000785 | 0.000768 | 0.000755 | 0.000744 | 0.000735
Z |  |  | 0.99969 | 0.99686 | 0.99371 | 0.99055 | 0.98737 | 0.98418 | 0.98098 | 0.97776 | 0.97453 | 0.96803 | 0.93461 | 0.89946 | 0.86218 | 0.82222 | 0.058354 | 0.07715 | 0.14992 | 0.21973 | 0.28734 | 0.35324
H |  | kJ/kg | 248.538 | 248.445 | 248.342 | 248.238 | 248.133 | 248.028 | 247.923 | 247.817 | 247.71 | 247.495 | 246.383 | 245.201 | 243.932 | 242.553 | 175.947 | 175.722 | 175.024 | 174.556 | 174.242 | 174.039
S |  | kJ/kg*K | 0.9253 | 0.8645 | 0.8461 | 0.8353 | 0.8275 | 0.8214 | 0.8165 | 0.8122 | 0.8085 | 0.8023 | 0.782 | 0.7692 | 0.7592 | 0.7507 | 0.5739 | 0.5728 | 0.569 | 0.5658 | 0.5631 | 0.5607
CP |  | kJ/kg*K | 0.9441 | 0.9445 | 0.945 | 0.9455 | 0.9459 | 0.9464 | 0.9469 | 0.9474 | 0.9479 | 0.9489 | 0.9548 | 0.9619 | 0.9708 | 0.9824 | 1.274 | 1.2624 | 1.2279 | 1.2049 | 1.1881 | 1.1753
CP/CV |  |  | 1.0287 | 1.0291 | 1.0295 | 1.0299 | 1.0303 | 1.0307 | 1.0312 | 1.0316 | 1.0321 | 1.033 | 1.0383 | 1.0449 | 1.0534 | 1.0647 | 1.2839 | 1.2715 | 1.2346 | 1.2098 | 1.1916 | 1.1775
CS |  | m/s | 102.4582 | 102.1861 | 101.8823 | 101.5767 | 101.2693 | 100.9602 | 100.6493 | 100.3366 | 100.0219 | 99.3869 | 96.0872 | 92.5461 | 88.7037 | 84.4721 | 170.4572 | 175.1607 | 192.2249 | 207.2874 | 220.9766 | 233.6528
T | 120 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.097 | 0.97 | 1.945 | 2.927 | 3.915 | 4.909 | 5.909 | 6.915 | 7.928 | 9.974 | 20.628 | 32.088 | 44.524 | 58.175 | 1240.727 | 1249.502 | 1279.55 | 1304.174 | 1325.298 | 1343.94
V |  | kg/m3 | 10.3396 | 1.0312 | 0.51401 | 0.34163 | 0.25544 | 0.20372 | 0.16923 | 0.1446 | 0.12613 | 0.10026 | 0.048478 | 0.031165 | 0.02246 | 0.01719 | 0.000806 | 0.0008 | 0.000782 | 0.000767 | 0.000755 | 0.000744
Z |  |  | 0.9997 | 0.99699 | 0.99397 | 0.99093 | 0.98789 | 0.98483 | 0.98176 | 0.97868 | 0.97559 | 0.96936 | 0.93743 | 0.90396 | 0.86863 | 0.831 | 0.059371 | 0.078359 | 0.15151 | 0.22134 | 0.28879 | 0.3544
H |  | kJ/kg | 253.269 | 253.178 | 253.077 | 252.975 | 252.873 | 252.771 | 252.668 | 252.564 | 252.46 | 252.25 | 251.166 | 250.018 | 248.793 | 247.47 | 182.389 | 182.097 | 181.206 | 180.612 | 180.208 | 179.937
S |  | kJ/kg*K | 0.9374 | 0.8766 | 0.8582 | 0.8474 | 0.8396 | 0.8336 | 0.8286 | 0.8244 | 0.8207 | 0.8144 | 0.7943 | 0.7815 | 0.7717 | 0.7633 | 0.5904 | 0.5891 | 0.5848 | 0.5813 | 0.5784 | 0.5758
CP |  | kJ/kg*K | 0.9483 | 0.9487 | 0.9492 | 0.9496 | 0.9501 | 0.9505 | 0.951 | 0.9515 | 0.952 | 0.953 | 0.9586 | 0.9653 | 0.9737 | 0.9843 | 1.3041 | 1.2886 | 1.2451 | 1.2177 | 1.1985 | 1.1841
CP/CV |  |  | 1.0286 | 1.0289 | 1.0293 | 1.0297 | 1.0301 | 1.0305 | 1.0309 | 1.0314 | 1.0318 | 1.0327 | 1.0377 | 1.044 | 1.0518 | 1.0621 | 1.3115 | 1.2952 | 1.249 | 1.2196 | 1.1988 | 1.183
CS |  | m/s | 103.1106 | 102.8481 | 102.5549 | 102.2601 | 101.9638 | 101.6659 | 101.3663 | 101.0651 | 100.7622 | 100.1513 | 96.9852 | 93.6056 | 89.9636 | 85.9894 | 158.8193 | 163.9485 | 182.2018 | 197.9951 | 212.179 | 225.2109
T | 125 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.095 | 0.957 | 1.921 | 2.889 | 3.864 | 4.844 | 5.83 | 6.823 | 7.821 | 9.836 | 20.311 | 31.537 | 43.66 | 56.883 | 97.066 | 1222.372 | 1256.746 | 1283.963 | 1306.857 | 1326.806
V |  | kg/m3 | 10.4712 | 1.0444 | 0.52068 | 0.3461 | 0.25881 | 0.20644 | 0.17152 | 0.14657 | 0.12786 | 0.10167 | 0.049234 | 0.031709 | 0.022904 | 0.01758 | 0.010302 | 0.000818 | 0.000796 | 0.000779 | 0.000765 | 0.000754
Z |  |  | 0.99971 | 0.99711 | 0.99421 | 0.9913 | 0.98838 | 0.98545 | 0.98251 | 0.97955 | 0.97659 | 0.97063 | 0.9401 | 0.90821 | 0.87469 | 0.8392 | 0.73769 | 0.079887 | 0.15347 | 0.22333 | 0.2906 | 0.35591
H |  | kJ/kg | 258.021 | 257.932 | 257.834 | 257.734 | 257.634 | 257.534 | 257.433 | 257.332 | 257.23 | 257.025 | 255.969 | 254.854 | 253.669 | 252.397 | 248.663 | 188.619 | 187.479 | 186.735 | 186.227 | 185.88
S |  | kJ/kg*K | 0.9494 | 0.8887 | 0.8703 | 0.8594 | 0.8517 | 0.8456 | 0.8407 | 0.8364 | 0.8327 | 0.8265 | 0.8064 | 0.7937 | 0.784 | 0.7758 | 0.7579 | 0.6056 | 0.6007 | 0.5968 | 0.5936 | 0.5908
CP |  | kJ/kg*K | 0.9526 | 0.953 | 0.9534 | 0.9539 | 0.9543 | 0.9548 | 0.9552 | 0.9557 | 0.9562 | 0.9571 | 0.9625 | 0.9689 | 0.9767 | 0.9865 | 1.0283 | 1.3213 | 1.2648 | 1.2317 | 1.2095 | 1.1932
CP/CV |  |  | 1.0284 | 1.0288 | 1.0291 | 1.0295 | 1.0299 | 1.0303 | 1.0307 | 1.0311 | 1.0315 | 1.0324 | 1.0372 | 1.0431 | 1.0504 | 1.0597 | 1.1009 | 1.3253 | 1.2658 | 1.2305 | 1.2066 | 1.1889
CS |  | m/s | 103.7588 | 103.5053 | 103.2223 | 102.938 | 102.6522 | 102.365 | 102.0763 | 101.7862 | 101.4945 | 100.9065 | 97.8671 | 94.6388 | 91.1817 | 87.4402 | 76.1905 | 152.441 | 172.1648 | 188.8023 | 203.5359 | 216.9529
T | 130 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.094 | 0.946 | 1.896 | 2.852 | 3.814 | 4.781 | 5.754 | 6.732 | 7.716 | 9.702 | 20.005 | 31.008 | 42.839 | 55.669 | 93.986 | 1192.449 | 1232.621 | 1263.004 | 1287.952 | 1309.369
V |  | kg/m3 | 10.6028 | 1.0576 | 0.52734 | 0.35057 | 0.26219 | 0.20915 | 0.1738 | 0.14854 | 0.12959 | 0.10307 | 0.049986 | 0.032249 | 0.023343 | 0.017963 | 0.01064 | 0.000839 | 0.000811 | 0.000792 | 0.000776 | 0.000764
Z |  |  | 0.99972 | 0.99723 | 0.99444 | 0.99165 | 0.98885 | 0.98604 | 0.98322 | 0.98038 | 0.97754 | 0.97183 | 0.94263 | 0.91222 | 0.8804 | 0.84686 | 0.75241 | 0.081844 | 0.15588 | 0.22574 | 0.29281 | 0.35781
H |  | kJ/kg | 262.795 | 262.708 | 262.612 | 262.514 | 262.417 | 262.319 | 262.22 | 262.121 | 262.022 | 261.821 | 260.792 | 259.708 | 258.56 | 257.336 | 253.798 | 195.326 | 193.859 | 192.932 | 192.304 | 191.87
S |  | kJ/kg*K | 0.9613 | 0.9006 | 0.8822 | 0.8713 | 0.8636 | 0.8576 | 0.8526 | 0.8484 | 0.8447 | 0.8385 | 0.8184 | 0.8058 | 0.7962 | 0.7881 | 0.7707 | 0.6223 | 0.6166 | 0.6123 | 0.6088 | 0.6058
CP |  | kJ/kg*K | 0.957 | 0.9574 | 0.9578 | 0.9582 | 0.9587 | 0.9591 | 0.9595 | 0.96 | 0.9604 | 0.9614 | 0.9665 | 0.9726 | 0.98 | 0.9891 | 1.0258 | 1.3639 | 1.2877 | 1.2472 | 1.2212 | 1.2028
CP/CV |  |  | 1.0283 | 1.0286 | 1.029 | 1.0294 | 1.0297 | 1.0301 | 1.0305 | 1.0309 | 1.0313 | 1.0321 | 1.0367 | 1.0422 | 1.049 | 1.0576 | 1.0934 | 1.3653 | 1.2856 | 1.2427 | 1.215 | 1.1951
CS |  | m/s | 104.4026 | 104.1578 | 103.8847 | 103.6103 | 103.3347 | 103.0577 | 102.7795 | 102.4999 | 102.2189 | 101.6529 | 98.7338 | 95.6476 | 92.3616 | 88.8316 | 78.4471 | 140.4737 | 162.0728 | 179.6965 | 195.0431 | 208.8773
T | 135 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.093 | 0.934 | 1.873 | 2.817 | 3.766 | 4.72 | 5.679 | 6.644 | 7.615 | 9.572 | 19.71 | 30.501 | 42.057 | 54.525 | 91.206 | 1158.449 | 1206.816 | 1241.155 | 1268.518 | 1291.597
V |  | kg/m3 | 10.7344 | 1.0709 | 0.534 | 0.35504 | 0.26556 | 0.21187 | 0.17607 | 0.1505 | 0.13132 | 0.10447 | 0.050736 | 0.032785 | 0.023777 | 0.01834 | 0.010964 | 0.000863 | 0.000829 | 0.000806 | 0.000788 | 0.000774
Z |  |  | 0.99973 | 0.99734 | 0.99466 | 0.99198 | 0.9893 | 0.9866 | 0.98389 | 0.98118 | 0.97845 | 0.97298 | 0.94503 | 0.91602 | 0.88577 | 0.85404 | 0.76584 | 0.084415 | 0.15883 | 0.22864 | 0.29547 | 0.36012
H |  | kJ/kg | 267.591 | 267.506 | 267.412 | 267.317 | 267.221 | 267.125 | 267.029 | 266.932 | 266.835 | 266.639 | 265.635 | 264.581 | 263.469 | 262.288 | 258.923 | 202.285 | 200.363 | 199.209 | 198.441 | 197.909
S |  | kJ/kg*K | 0.9731 | 0.9124 | 0.894 | 0.8832 | 0.8755 | 0.8694 | 0.8645 | 0.8602 | 0.8566 | 0.8503 | 0.8304 | 0.8178 | 0.8083 | 0.8003 | 0.7834 | 0.6395 | 0.6326 | 0.6278 | 0.6239 | 0.6207
CP |  | kJ/kg*K | 0.9615 | 0.9618 | 0.9623 | 0.9627 | 0.9631 | 0.9635 | 0.9639 | 0.9644 | 0.9648 | 0.9657 | 0.9707 | 0.9765 | 0.9834 | 0.9919 | 1.0245 | 1.4233 | 1.3148 | 1.2643 | 1.2338 | 1.2129
CP/CV |  |  | 1.0282 | 1.0285 | 1.0288 | 1.0292 | 1.0295 | 1.0299 | 1.0303 | 1.0307 | 1.031 | 1.0318 | 1.0362 | 1.0414 | 1.0478 | 1.0557 | 1.0871 | 1.4223 | 1.3096 | 1.2565 | 1.224 | 1.2016
CS |  | m/s | 105.0422 | 104.8058 | 104.5422 | 104.2774 | 104.0114 | 103.7443 | 103.476 | 103.2065 | 102.9358 | 102.3907 | 99.586 | 96.6334 | 93.5065 | 90.1696 | 80.5355 | 127.7763 | 151.8737 | 170.6647 | 186.6975 | 200.9836
T | 140 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.092 | 0.922 | 1.85 | 2.782 | 3.718 | 4.66 | 5.607 | 6.559 | 7.516 | 9.445 | 19.424 | 30.014 | 41.312 | 53.443 | 88.675 | 135.76 | 1178.821 | 1218.234 | 1248.475 | 1273.453
V |  | kg/m3 | 10.8661 | 1.0841 | 0.54066 | 0.35951 | 0.26893 | 0.21458 | 0.17835 | 0.15246 | 0.13305 | 0.10587 | 0.051482 | 0.033318 | 0.024206 | 0.018712 | 0.011277 | 0.007366 | 0.000848 | 0.000821 | 0.000801 | 0.000785
Z |  |  | 0.99974 | 0.99744 | 0.99488 | 0.9923 | 0.98972 | 0.98713 | 0.98454 | 0.98193 | 0.97932 | 0.97408 | 0.94732 | 0.91963 | 0.89085 | 0.86079 | 0.77817 | 0.67771 | 0.16249 | 0.23211 | 0.29862 | 0.36287
H |  | kJ/kg | 272.41 | 272.327 | 272.234 | 272.141 | 272.048 | 271.954 | 271.86 | 271.765 | 271.67 | 271.479 | 270.499 | 269.473 | 268.395 | 267.255 | 264.045 | 259.969 | 207.017 | 205.578 | 204.643 | 203.999
S |  | kJ/kg*K | 0.9849 | 0.9241 | 0.9058 | 0.8949 | 0.8872 | 0.8812 | 0.8762 | 0.872 | 0.8683 | 0.8621 | 0.8422 | 0.8298 | 0.8203 | 0.8124 | 0.7958 | 0.7804 | 0.6488 | 0.6433 | 0.639 | 0.6355
CP |  | kJ/kg*K | 0.966 | 0.9664 | 0.9668 | 0.9672 | 0.9676 | 0.968 | 0.9684 | 0.9688 | 0.9693 | 0.9701 | 0.9749 | 0.9805 | 0.987 | 0.9949 | 1.0242 | 1.0882 | 1.3478 | 1.2834 | 1.2472 | 1.2234
CP/CV |  |  | 1.028 | 1.0283 | 1.0287 | 1.029 | 1.0294 | 1.0297 | 1.0301 | 1.0304 | 1.0308 | 1.0316 | 1.0357 | 1.0407 | 1.0466 | 1.0539 | 1.0818 | 1.1451 | 1.3394 | 1.2721 | 1.2339 | 1.2085
CS |  | m/s | 105.6777 | 105.4494 | 105.1948 | 104.9392 | 104.6826 | 104.4249 | 104.1662 | 103.9064 | 103.6455 | 103.1204 | 100.4244 | 97.5978 | 94.6189 | 91.4593 | 82.4837 | 70.8444 | 141.498 | 161.6931 | 178.4974 | 193.2726
T | 145 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.091 | 0.911 | 1.827 | 2.747 | 3.672 | 4.602 | 5.537 | 6.476 | 7.42 | 9.323 | 19.148 | 29.545 | 40.599 | 52.418 | 86.353 | 130.278 | 1147.87 | 1194.006 | 1227.725 | 1254.889
V |  | kg/m3 | 10.9977 | 1.0973 | 0.54731 | 0.36397 | 0.2723 | 0.21729 | 0.18062 | 0.15442 | 0.13478 | 0.10727 | 0.052224 | 0.033846 | 0.024631 | 0.019078 | 0.01158 | 0.007676 | 0.000871 | 0.000838 | 0.000815 | 0.000797
Z |  |  | 0.99975 | 0.99754 | 0.99508 | 0.99261 | 0.99013 | 0.98765 | 0.98515 | 0.98266 | 0.98015 | 0.97512 | 0.9495 | 0.92305 | 0.89564 | 0.86713 | 0.78955 | 0.69778 | 0.16708 | 0.23626 | 0.30232 | 0.3661
H |  | kJ/kg | 277.252 | 277.17 | 277.08 | 276.989 | 276.897 | 276.805 | 276.713 | 276.621 | 276.528 | 276.341 | 275.384 | 274.385 | 273.339 | 272.237 | 269.167 | 265.382 | 213.855 | 212.047 | 210.915 | 210.144
S |  | kJ/kg*K | 0.9965 | 0.9358 | 0.9174 | 0.9066 | 0.8989 | 0.8928 | 0.8879 | 0.8837 | 0.88 | 0.8738 | 0.854 | 0.8416 | 0.8322 | 0.8244 | 0.8082 | 0.7935 | 0.6653 | 0.6588 | 0.6541 | 0.6503
CP |  | kJ/kg*K | 0.9707 | 0.971 | 0.9714 | 0.9718 | 0.9722 | 0.9726 | 0.973 | 0.9734 | 0.9738 | 0.9747 | 0.9793 | 0.9846 | 0.9908 | 0.9981 | 1.0247 | 1.0774 | 1.3894 | 1.3049 | 1.2616 | 1.2344
CP/CV |  |  | 1.0279 | 1.0282 | 1.0285 | 1.0288 | 1.0292 | 1.0295 | 1.0299 | 1.0302 | 1.0306 | 1.0313 | 1.0353 | 1.04 | 1.0456 | 1.0523 | 1.0773 | 1.1289 | 1.3778 | 1.2901 | 1.2446 | 1.2157
CS |  | m/s | 106.3091 | 106.0886 | 105.8428 | 105.596 | 105.3484 | 105.0997 | 104.8502 | 104.5997 | 104.3482 | 103.8422 | 101.2498 | 98.5421 | 95.7014 | 92.705 | 84.3134 | 73.8423 | 130.849 | 152.768 | 170.4427 | 185.7468
T | 150 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.09 | 0.9 | 1.805 | 2.714 | 3.628 | 4.546 | 5.468 | 6.395 | 7.326 | 9.203 | 18.881 | 29.094 | 39.917 | 51.444 | 84.208 | 125.525 | 1112.752 | 1168.157 | 1206.15 | 1235.853
V |  | kg/m3 | 11.1293 | 1.1106 | 0.55396 | 0.36843 | 0.27566 | 0.22 | 0.18289 | 0.15638 | 0.1365 | 0.10866 | 0.052964 | 0.034371 | 0.025052 | 0.019439 | 0.011875 | 0.007967 | 0.000899 | 0.000856 | 0.000829 | 0.000809
Z |  |  | 0.99976 | 0.99764 | 0.99527 | 0.9929 | 0.99052 | 0.98813 | 0.98574 | 0.98335 | 0.98094 | 0.97611 | 0.95157 | 0.92629 | 0.90018 | 0.87311 | 0.80009 | 0.71565 | 0.17295 | 0.24123 | 0.30665 | 0.36986
H |  | kJ/kg | 282.117 | 282.037 | 281.948 | 281.859 | 281.77 | 281.68 | 281.59 | 281.499 | 281.408 | 281.226 | 280.291 | 279.319 | 278.303 | 277.237 | 274.293 | 270.75 | 220.933 | 218.631 | 217.261 | 216.344
S |  | kJ/kg*K | 1.0081 | 0.9474 | 0.929 | 0.9182 | 0.9105 | 0.9044 | 0.8995 | 0.8953 | 0.8916 | 0.8854 | 0.8656 | 0.8533 | 0.844 | 0.8363 | 0.8203 | 0.8062 | 0.6821 | 0.6745 | 0.6692 | 0.665
CP |  | kJ/kg*K | 0.9754 | 0.9757 | 0.9761 | 0.9765 | 0.9769 | 0.9772 | 0.9776 | 0.978 | 0.9784 | 0.9793 | 0.9837 | 0.9888 | 0.9947 | 1.0016 | 1.0258 | 1.0704 | 1.4446 | 1.3294 | 1.2771 | 1.2459
CP/CV |  |  | 1.0278 | 1.028 | 1.0283 | 1.0287 | 1.029 | 1.0293 | 1.0296 | 1.03 | 1.0303 | 1.031 | 1.0348 | 1.0393 | 1.0445 | 1.0508 | 1.0734 | 1.1164 | 1.4297 | 1.3109 | 1.2563 | 1.2233
CS |  | m/s | 106.9366 | 106.7236 | 106.4861 | 106.2479 | 106.0088 | 105.7689 | 105.5281 | 105.2865 | 105.044 | 104.5564 | 102.0627 | 99.4674 | 96.756 | 93.9106 | 86.0411 | 76.5253 | 119.7843 | 143.8753 | 162.5359 | 178.4105
T | 155 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.089 | 0.89 | 1.784 | 2.682 | 3.584 | 4.49 | 5.401 | 6.316 | 7.235 | 9.087 | 18.622 | 28.659 | 39.264 | 50.517 | 82.218 | 121.33 | 1071.405 | 1140.275 | 1183.605 | 1216.282
V |  | kg/m3 | 11.2609 | 1.1238 | 0.56061 | 0.37289 | 0.27902 | 0.2227 | 0.18515 | 0.15833 | 0.13822 | 0.11005 | 0.053701 | 0.034893 | 0.025469 | 0.019795 | 0.012163 | 0.008242 | 0.000933 | 0.000877 | 0.000845 | 0.000822
Z |  |  | 0.99977 | 0.99773 | 0.99546 | 0.99318 | 0.99089 | 0.9886 | 0.98631 | 0.984 | 0.9817 | 0.97706 | 0.95355 | 0.92938 | 0.90448 | 0.87875 | 0.80989 | 0.73174 | 0.18075 | 0.24721 | 0.3117 | 0.37419
H |  | kJ/kg | 287.006 | 286.928 | 286.841 | 286.753 | 286.666 | 286.578 | 286.49 | 286.401 | 286.312 | 286.134 | 285.221 | 284.273 | 283.286 | 282.254 | 279.426 | 276.089 | 228.34 | 225.347 | 223.688 | 222.604
S |  | kJ/kg*K | 1.0196 | 0.9589 | 0.9405 | 0.9297 | 0.922 | 0.9159 | 0.911 | 0.9068 | 0.9031 | 0.897 | 0.8772 | 0.8649 | 0.8557 | 0.848 | 0.8324 | 0.8188 | 0.6995 | 0.6903 | 0.6843 | 0.6797
CP |  | kJ/kg*K | 0.9802 | 0.9805 | 0.9809 | 0.9812 | 0.9816 | 0.982 | 0.9824 | 0.9827 | 0.9831 | 0.9839 | 0.9882 | 0.9931 | 0.9987 | 1.0052 | 1.0274 | 1.0658 | 1.5235 | 1.3577 | 1.2938 | 1.2579
CP/CV |  |  | 1.0276 | 1.0279 | 1.0282 | 1.0285 | 1.0288 | 1.0291 | 1.0294 | 1.0298 | 1.0301 | 1.0308 | 1.0344 | 1.0386 | 1.0436 | 1.0494 | 1.0699 | 1.1066 | 1.5051 | 1.3354 | 1.269 | 1.2313
CS |  | m/s | 107.5602 | 107.3544 | 107.125 | 106.895 | 106.6641 | 106.4326 | 106.2003 | 105.9672 | 105.7333 | 105.2633 | 102.8638 | 100.3749 | 97.7848 | 95.0792 | 87.6801 | 78.9644 | 108.0761 | 135.0027 | 154.7829 | 171.2703
T | 160 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.088 | 0.879 | 1.763 | 2.65 | 3.541 | 4.436 | 5.336 | 6.239 | 7.146 | 8.973 | 18.37 | 28.239 | 38.636 | 49.633 | 80.362 | 117.578 | 1019.867 | 1109.805 | 1159.915 | 1196.104
V |  | kg/m3 | 11.3925 | 1.137 | 0.56726 | 0.37734 | 0.28238 | 0.2254 | 0.18742 | 0.16028 | 0.13993 | 0.11144 | 0.054436 | 0.035412 | 0.025882 | 0.020148 | 0.012444 | 0.008505 | 0.000981 | 0.000901 | 0.000862 | 0.000836
Z |  |  | 0.99978 | 0.99782 | 0.99563 | 0.99344 | 0.99125 | 0.98905 | 0.98684 | 0.98463 | 0.98242 | 0.97797 | 0.95543 | 0.93231 | 0.90855 | 0.88408 | 0.81903 | 0.74638 | 0.19175 | 0.25444 | 0.31757 | 0.37915
H |  | kJ/kg | 291.919 | 291.842 | 291.757 | 291.672 | 291.586 | 291.5 | 291.413 | 291.327 | 291.24 | 291.065 | 290.174 | 289.25 | 288.29 | 287.289 | 284.568 | 281.411 | 236.246 | 232.216 | 230.201 | 228.924
S |  | kJ/kg*K | 1.031 | 0.9703 | 0.9519 | 0.9411 | 0.9334 | 0.9274 | 0.9224 | 0.9182 | 0.9146 | 0.9084 | 0.8887 | 0.8765 | 0.8673 | 0.8597 | 0.8443 | 0.8311 | 0.7179 | 0.7062 | 0.6994 | 0.6944
CP |  | kJ/kg*K | 0.985 | 0.9854 | 0.9857 | 0.9861 | 0.9864 | 0.9868 | 0.9872 | 0.9875 | 0.9879 | 0.9887 | 0.9928 | 0.9975 | 1.0028 | 1.009 | 1.0295 | 1.0631 | 1.6504 | 1.3907 | 1.3117 | 1.2703
CP/CV |  |  | 1.0275 | 1.0277 | 1.028 | 1.0283 | 1.0286 | 1.0289 | 1.0292 | 1.0295 | 1.0299 | 1.0305 | 1.034 | 1.038 | 1.0427 | 1.0482 | 1.0668 | 1.0986 | 1.6282 | 1.3645 | 1.2829 | 1.2396
CS |  | m/s | 108.1799 | 107.9811 | 107.7595 | 107.5373 | 107.3145 | 107.0909 | 106.8667 | 106.6419 | 106.4163 | 105.9631 | 103.6535 | 101.2654 | 98.7893 | 96.214 | 89.241 | 81.2081 | 95.3171 | 126.1415 | 147.1939 | 164.3354
T | 165 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.087 | 0.869 | 1.742 | 2.619 | 3.5 | 4.384 | 5.272 | 6.164 | 7.06 | 8.863 | 18.127 | 27.833 | 38.033 | 48.788 | 78.624 | 114.186 | 948.757 | 1076 | 1134.874 | 1175.236
V |  | kg/m3 | 11.5241 | 1.1502 | 0.57391 | 0.3818 | 0.28574 | 0.2281 | 0.18968 | 0.16223 | 0.14165 | 0.11283 | 0.055167 | 0.035928 | 0.026293 | 0.020497 | 0.012719 | 0.008758 | 0.001054 | 0.000929 | 0.000881 | 0.000851
Z |  |  | 0.99979 | 0.9979 | 0.9958 | 0.9937 | 0.99159 | 0.98947 | 0.98736 | 0.98523 | 0.98311 | 0.97884 | 0.95722 | 0.9351 | 0.91242 | 0.88912 | 0.82758 | 0.75978 | 0.20913 | 0.26329 | 0.32438 | 0.38479
H |  | kJ/kg | 296.856 | 296.782 | 296.698 | 296.614 | 296.53 | 296.446 | 296.361 | 296.277 | 296.191 | 296.021 | 295.149 | 294.248 | 293.314 | 292.343 | 289.721 | 286.722 | 245.046 | 239.264 | 236.807 | 235.307
S |  | kJ/kg*K | 1.0423 | 0.9816 | 0.9632 | 0.9524 | 0.9447 | 0.9387 | 0.9338 | 0.9296 | 0.9259 | 0.9198 | 0.9001 | 0.888 | 0.8788 | 0.8713 | 0.8562 | 0.8433 | 0.7381 | 0.7224 | 0.7146 | 0.7091
CP |  | kJ/kg*K | 0.99 | 0.9903 | 0.9906 | 0.991 | 0.9913 | 0.9917 | 0.992 | 0.9924 | 0.9928 | 0.9935 | 0.9975 | 1.002 | 1.0071 | 1.0129 | 1.0319 | 1.0617 | 1.906 | 1.4298 | 1.3309 | 1.2831
CP/CV |  |  | 1.0273 | 1.0276 | 1.0279 | 1.0281 | 1.0284 | 1.0287 | 1.029 | 1.0293 | 1.0296 | 1.0303 | 1.0336 | 1.0374 | 1.0418 | 1.047 | 1.0641 | 1.0919 | 1.8795 | 1.3995 | 1.2979 | 1.2482
CS |  | m/s | 108.7959 | 108.6038 | 108.3897 | 108.1751 | 107.9599 | 107.7441 | 107.5277 | 107.3107 | 107.0931 | 106.656 | 104.4324 | 102.14 | 99.7713 | 97.3173 | 90.7328 | 83.2911 | 80.6292 | 117.2929 | 139.786 | 157.6183
T | 170 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.086 | 0.86 | 1.723 | 2.589 | 3.459 | 4.333 | 5.21 | 6.091 | 6.975 | 8.756 | 17.89 | 27.441 | 37.454 | 47.98 | 76.991 | 111.092 | 821.892 | 1037.859 | 1108.242 | 1153.588
V |  | kg/m3 | 11.6557 | 1.1635 | 0.58055 | 0.38625 | 0.28909 | 0.2308 | 0.19194 | 0.16418 | 0.14336 | 0.11421 | 0.055897 | 0.036442 | 0.0267 | 0.020842 | 0.012989 | 0.009002 | 0.001217 | 0.000964 | 0.000902 | 0.000867
Z |  |  | 0.9998 | 0.99798 | 0.99596 | 0.99394 | 0.99191 | 0.98988 | 0.98785 | 0.98581 | 0.98377 | 0.97967 | 0.95894 | 0.93776 | 0.9161 | 0.89389 | 0.83559 | 0.77213 | 0.24679 | 0.27426 | 0.33229 | 0.3912
H |  | kJ/kg | 301.819 | 301.745 | 301.664 | 301.581 | 301.499 | 301.417 | 301.334 | 301.251 | 301.168 | 301 | 300.149 | 299.27 | 298.361 | 297.418 | 294.887 | 292.03 | 256.274 | 246.527 | 243.512 | 241.756
S |  | kJ/kg*K | 1.0536 | 0.9929 | 0.9745 | 0.9637 | 0.956 | 0.95 | 0.9451 | 0.9409 | 0.9372 | 0.9311 | 0.9115 | 0.8994 | 0.8903 | 0.8829 | 0.8679 | 0.8554 | 0.7635 | 0.7389 | 0.7298 | 0.7237
CP |  | kJ/kg*K | 0.995 | 0.9953 | 0.9956 | 0.9959 | 0.9963 | 0.9966 | 0.997 | 0.9973 | 0.9977 | 0.9984 | 1.0023 | 1.0066 | 1.0115 | 1.017 | 1.0346 | 1.0613 | 2.8687 | 1.4765 | 1.3514 | 1.2963
CP/CV |  |  | 1.0272 | 1.0274 | 1.0277 | 1.028 | 1.0283 | 1.0285 | 1.0288 | 1.0291 | 1.0294 | 1.03 | 1.0332 | 1.0369 | 1.041 | 1.0458 | 1.0616 | 1.0862 | 2.8344 | 1.4419 | 1.3141 | 1.257
CS |  | m/s | 109.4083 | 109.2226 | 109.0157 | 108.8084 | 108.6005 | 108.3922 | 108.1833 | 107.9738 | 107.7639 | 107.3423 | 105.2009 | 102.9994 | 100.7319 | 98.3914 | 92.1628 | 85.2394 | 61.2506 | 108.479 | 132.5846 | 151.1354
T | 175 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.085 | 0.85 | 1.703 | 2.56 | 3.419 | 4.283 | 5.149 | 6.02 | 6.893 | 8.651 | 17.66 | 27.062 | 36.895 | 47.205 | 75.452 | 108.251 | 416.208 | 994.066 | 1079.752 | 1131.065
V |  | kg/m3 | 11.7873 | 1.1767 | 0.58719 | 0.3907 | 0.29245 | 0.2335 | 0.1942 | 0.16613 | 0.14507 | 0.11559 | 0.056624 | 0.036952 | 0.027104 | 0.021184 | 0.013253 | 0.009238 | 0.002403 | 0.001006 | 0.000926 | 0.000884
Z |  |  | 0.99981 | 0.99806 | 0.99612 | 0.99418 | 0.99223 | 0.99028 | 0.98832 | 0.98636 | 0.9844 | 0.98047 | 0.96057 | 0.94029 | 0.91959 | 0.89842 | 0.84313 | 0.78356 | 0.40759 | 0.28807 | 0.34147 | 0.39843
H |  | kJ/kg | 306.806 | 306.734 | 306.654 | 306.574 | 306.493 | 306.412 | 306.331 | 306.25 | 306.169 | 306.005 | 305.172 | 304.315 | 303.429 | 302.513 | 300.068 | 297.337 | 276.096 | 254.045 | 250.323 | 248.27
S |  | kJ/kg*K | 1.0648 | 1.0041 | 0.9857 | 0.9749 | 0.9672 | 0.9612 | 0.9563 | 0.9521 | 0.9485 | 0.9423 | 0.9228 | 0.9107 | 0.9017 | 0.8943 | 0.8795 | 0.8673 | 0.808 | 0.7557 | 0.7451 | 0.7383
CP |  | kJ/kg*K | 1 | 1.0003 | 1.0007 | 1.001 | 1.0013 | 1.0017 | 1.002 | 1.0023 | 1.0027 | 1.0034 | 1.0071 | 1.0113 | 1.0159 | 1.0212 | 1.0377 | 1.0617 | 2.5406 | 1.5324 | 1.3729 | 1.3096
CP/CV |  |  | 1.027 | 1.0273 | 1.0275 | 1.0278 | 1.0281 | 1.0284 | 1.0286 | 1.0289 | 1.0292 | 1.0298 | 1.0329 | 1.0363 | 1.0403 | 1.0448 | 1.0594 | 1.0813 | 2.5361 | 1.4933 | 1.3312 | 1.2659
CS |  | m/s | 110.017 | 109.8375 | 109.6376 | 109.4373 | 109.2366 | 109.0354 | 108.8337 | 108.6315 | 108.4289 | 108.0222 | 105.9595 | 103.8445 | 101.6726 | 99.4385 | 93.537 | 87.0728 | 48.5832 | 99.7689 | 125.6276 | 144.9073
T | 180 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.084 | 0.84 | 1.684 | 2.531 | 3.381 | 4.234 | 5.09 | 5.95 | 6.813 | 8.549 | 17.437 | 26.695 | 36.356 | 46.462 | 73.997 | 105.625 | 344.323 | 943.035 | 1049.124 | 1107.57
V |  | kg/m3 | 11.9189 | 1.1899 | 0.59383 | 0.39515 | 0.2958 | 0.23619 | 0.19645 | 0.16807 | 0.14678 | 0.11697 | 0.057349 | 0.037461 | 0.027505 | 0.021523 | 0.013514 | 0.009467 | 0.002904 | 0.00106 | 0.000953 | 0.000903
Z |  |  | 0.99981 | 0.99814 | 0.99627 | 0.9944 | 0.99253 | 0.99065 | 0.98877 | 0.98689 | 0.98501 | 0.98123 | 0.96214 | 0.94271 | 0.92291 | 0.90272 | 0.85022 | 0.79418 | 0.48724 | 0.30572 | 0.35212 | 0.40657
H |  | kJ/kg | 311.819 | 311.749 | 311.67 | 311.591 | 311.512 | 311.433 | 311.354 | 311.274 | 311.195 | 311.034 | 310.22 | 309.383 | 308.52 | 307.63 | 305.264 | 302.648 | 285.72 | 261.865 | 257.243 | 254.852
S |  | kJ/kg*K | 1.0759 | 1.0152 | 0.9968 | 0.986 | 0.9784 | 0.9724 | 0.9674 | 0.9633 | 0.9596 | 0.9535 | 0.934 | 0.9219 | 0.913 | 0.9056 | 0.8911 | 0.879 | 0.8294 | 0.7731 | 0.7604 | 0.7529
CP |  | kJ/kg*K | 1.0052 | 1.0054 | 1.0058 | 1.0061 | 1.0064 | 1.0067 | 1.0071 | 1.0074 | 1.0077 | 1.0084 | 1.012 | 1.016 | 1.0205 | 1.0255 | 1.0409 | 1.0628 | 1.6124 | 1.5971 | 1.3952 | 1.3229
CP/CV |  |  | 1.0269 | 1.0271 | 1.0274 | 1.0276 | 1.0279 | 1.0282 | 1.0284 | 1.0287 | 1.029 | 1.0295 | 1.0325 | 1.0358 | 1.0396 | 1.0438 | 1.0573 | 1.0771 | 1.6084 | 1.5533 | 1.3489 | 1.2746
CS |  | m/s | 110.6222 | 110.4487 | 110.2555 | 110.062 | 109.8681 | 109.6737 | 109.479 | 109.2838 | 109.0883 | 108.6959 | 106.7085 | 104.6759 | 102.5945 | 100.4602 | 94.8609 | 88.8068 | 56.5141 | 91.3306 | 118.9689 | 138.9599
T | 185 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.083 | 0.831 | 1.665 | 2.503 | 3.343 | 4.186 | 5.032 | 5.882 | 6.735 | 8.449 | 17.22 | 26.339 | 35.837 | 45.748 | 72.618 | 103.185 | 309.649 | 883.325 | 1016.102 | 1083.014
V |  | kg/m3 | 12.0505 | 1.2031 | 0.60047 | 0.39959 | 0.29915 | 0.23889 | 0.19871 | 0.17001 | 0.14849 | 0.11835 | 0.058072 | 0.037966 | 0.027904 | 0.021859 | 0.013771 | 0.009691 | 0.003229 | 0.001132 | 0.000984 | 0.000923
Z |  |  | 0.99982 | 0.99821 | 0.99641 | 0.99461 | 0.99281 | 0.99101 | 0.9892 | 0.9874 | 0.98558 | 0.98195 | 0.96363 | 0.94502 | 0.92608 | 0.9068 | 0.85691 | 0.80408 | 0.53589 | 0.32853 | 0.36445 | 0.41568
H |  | kJ/kg | 316.858 | 316.789 | 316.712 | 316.635 | 316.557 | 316.48 | 316.402 | 316.324 | 316.246 | 316.089 | 315.293 | 314.475 | 313.634 | 312.768 | 310.477 | 307.966 | 293.179 | 270.02 | 264.274 | 261.499
S |  | kJ/kg*K | 1.0869 | 1.0263 | 1.0079 | 0.9971 | 0.9894 | 0.9834 | 0.9785 | 0.9743 | 0.9707 | 0.9646 | 0.9451 | 0.9331 | 0.9242 | 0.9169 | 0.9025 | 0.8907 | 0.8458 | 0.791 | 0.7759 | 0.7675
CP |  | kJ/kg*K | 1.0103 | 1.0106 | 1.0109 | 1.0112 | 1.0116 | 1.0119 | 1.0122 | 1.0125 | 1.0129 | 1.0135 | 1.017 | 1.0209 | 1.0252 | 1.0299 | 1.0444 | 1.0645 | 1.4044 | 1.6641 | 1.4173 | 1.3359
CP/CV |  |  | 1.0268 | 1.027 | 1.0272 | 1.0275 | 1.0277 | 1.028 | 1.0282 | 1.0285 | 1.0288 | 1.0293 | 1.0321 | 1.0353 | 1.0389 | 1.0429 | 1.0555 | 1.0733 | 1.3968 | 1.6159 | 1.3665 | 1.2831
CS |  | m/s | 111.2239 | 111.0562 | 110.8695 | 110.6825 | 110.4951 | 110.3074 | 110.1194 | 109.931 | 109.7422 | 109.3636 | 107.4483 | 105.4943 | 103.4986 | 101.4583 | 96.139 | 90.4539 | 62.3606 | 83.5276 | 112.6827 | 133.3241
T | 190 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.082 | 0.822 | 1.647 | 2.475 | 3.306 | 4.139 | 4.976 | 5.816 | 6.658 | 8.352 | 17.009 | 25.994 | 35.335 | 45.061 | 71.309 | 100.909 | 286.524 | 815.015 | 980.509 | 1057.326
V |  | kg/m3 | 12.1821 | 1.2163 | 0.60711 | 0.40404 | 0.3025 | 0.24158 | 0.20096 | 0.17195 | 0.15019 | 0.11973 | 0.058792 | 0.03847 | 0.028301 | 0.022192 | 0.014024 | 0.00991 | 0.00349 | 0.001227 | 0.00102 | 0.000946
Z |  |  | 0.99983 | 0.99828 | 0.99655 | 0.99482 | 0.99309 | 0.99135 | 0.98962 | 0.98788 | 0.98614 | 0.98265 | 0.96506 | 0.94722 | 0.9291 | 0.91068 | 0.86322 | 0.81334 | 0.57289 | 0.35765 | 0.37867 | 0.42584
H |  | kJ/kg | 321.923 | 321.855 | 321.78 | 321.704 | 321.628 | 321.552 | 321.476 | 321.4 | 321.323 | 321.17 | 320.39 | 319.592 | 318.772 | 317.929 | 315.708 | 313.294 | 299.944 | 278.477 | 271.413 | 268.21
S |  | kJ/kg*K | 1.0979 | 1.0373 | 1.0189 | 1.0081 | 1.0004 | 0.9944 | 0.9895 | 0.9854 | 0.9817 | 0.9756 | 0.9562 | 0.9442 | 0.9353 | 0.9281 | 0.9139 | 0.9023 | 0.8604 | 0.8093 | 0.7914 | 0.7821
CP |  | kJ/kg*K | 1.0156 | 1.0159 | 1.0162 | 1.0165 | 1.0168 | 1.0171 | 1.0174 | 1.0177 | 1.018 | 1.0187 | 1.0221 | 1.0258 | 1.0299 | 1.0344 | 1.0481 | 1.0666 | 1.3119 | 1.7125 | 1.4381 | 1.3484
CP/CV |  |  | 1.0266 | 1.0268 | 1.0271 | 1.0273 | 1.0276 | 1.0278 | 1.028 | 1.0283 | 1.0285 | 1.0291 | 1.0318 | 1.0348 | 1.0382 | 1.042 | 1.0538 | 1.07 | 1.3 | 1.6603 | 1.3827 | 1.2908
CS |  | m/s | 111.8221 | 111.66 | 111.4796 | 111.2989 | 111.1179 | 110.9366 | 110.755 | 110.573 | 110.3908 | 110.0254 | 108.1794 | 106.3002 | 104.3859 | 102.4341 | 97.3751 | 92.0242 | 67.0345 | 77.025 | 106.8668 | 128.0361
T | 195 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.081 | 0.813 | 1.629 | 2.448 | 3.27 | 4.094 | 4.921 | 5.751 | 6.584 | 8.257 | 16.804 | 25.66 | 34.849 | 44.4 | 70.062 | 98.777 | 269.173 | 742.04 | 942.346 | 1030.468
V |  | kg/m3 | 12.3137 | 1.2295 | 0.61374 | 0.40848 | 0.30585 | 0.24427 | 0.20321 | 0.17389 | 0.1519 | 0.1211 | 0.059511 | 0.038972 | 0.028695 | 0.022523 | 0.014273 | 0.010124 | 0.003715 | 0.001348 | 0.001061 | 0.00097
Z |  |  | 0.99983 | 0.99834 | 0.99668 | 0.99502 | 0.99335 | 0.99168 | 0.99001 | 0.98834 | 0.98667 | 0.98332 | 0.96643 | 0.94932 | 0.93197 | 0.91438 | 0.8692 | 0.82203 | 0.60331 | 0.39288 | 0.39494 | 0.43711
H |  | kJ/kg | 327.014 | 326.948 | 326.874 | 326.799 | 326.725 | 326.651 | 326.576 | 326.501 | 326.426 | 326.276 | 325.514 | 324.733 | 323.933 | 323.113 | 320.959 | 318.632 | 306.363 | 287.057 | 278.65 | 274.981
S |  | kJ/kg*K | 1.1089 | 1.0482 | 1.0298 | 1.0191 | 1.0114 | 1.0054 | 1.0005 | 0.9963 | 0.9927 | 0.9866 | 0.9672 | 0.9553 | 0.9464 | 0.9393 | 0.9251 | 0.9137 | 0.8742 | 0.8278 | 0.8069 | 0.7966
CP |  | kJ/kg*K | 1.0209 | 1.0211 | 1.0214 | 1.0217 | 1.022 | 1.0223 | 1.0226 | 1.023 | 1.0233 | 1.0239 | 1.0272 | 1.0308 | 1.0347 | 1.039 | 1.052 | 1.0691 | 1.2601 | 1.7087 | 1.4556 | 1.3597
CP/CV |  |  | 1.0265 | 1.0267 | 1.0269 | 1.0271 | 1.0274 | 1.0276 | 1.0279 | 1.0281 | 1.0283 | 1.0288 | 1.0315 | 1.0344 | 1.0376 | 1.0412 | 1.0522 | 1.067 | 1.2436 | 1.6541 | 1.3956 | 1.2974
CS |  | m/s | 112.4171 | 112.2603 | 112.0859 | 111.9113 | 111.7364 | 111.5613 | 111.3858 | 111.2102 | 111.0342 | 110.6816 | 108.902 | 107.0944 | 105.2572 | 103.3891 | 98.5727 | 93.5263 | 70.9771 | 72.6698 | 101.6406 | 123.1364
T | 200 | °C
P |  | bars | 0.01 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 1 | 2 | 3 | 4 | 5 | 7.5 | 10 | 20 | 30 | 40 | 50
r |  | kg/m3 | 0.08 | 0.805 | 1.612 | 2.422 | 3.234 | 4.049 | 4.867 | 5.687 | 6.511 | 8.165 | 16.603 | 25.335 | 34.38 | 43.762 | 68.873 | 96.772 | 255.311 | 672.087 | 901.899 | 1002.455
V |  | kg/m3 | 12.4453 | 1.2427 | 0.62038 | 0.41292 | 0.30919 | 0.24695 | 0.20546 | 0.17583 | 0.1536 | 0.12248 | 0.060228 | 0.039471 | 0.029087 | 0.022851 | 0.014519 | 0.010334 | 0.003917 | 0.001488 | 0.001109 | 0.000998
Z |  |  | 0.99984 | 0.9984 | 0.99681 | 0.99521 | 0.9936 | 0.992 | 0.9904 | 0.98879 | 0.98718 | 0.98396 | 0.96774 | 0.95133 | 0.93472 | 0.9179 | 0.87485 | 0.83019 | 0.62934 | 0.43152 | 0.41333 | 0.4495
H |  | kJ/kg | 332.132 | 332.067 | 331.994 | 331.921 | 331.849 | 331.776 | 331.703 | 331.629 | 331.556 | 331.409 | 330.662 | 329.9 | 329.119 | 328.32 | 326.229 | 323.985 | 312.577 | 295.46 | 285.96 | 281.804
S |  | kJ/kg*K | 1.1197 | 1.0591 | 1.0407 | 1.0299 | 1.0223 | 1.0163 | 1.0114 | 1.0072 | 1.0036 | 0.9975 | 0.9781 | 0.9662 | 0.9575 | 0.9503 | 0.9363 | 0.9251 | 0.8874 | 0.8456 | 0.8224 | 0.8111
CP |  | kJ/kg*K | 1.0262 | 1.0265 | 1.0268 | 1.0271 | 1.0274 | 1.0277 | 1.0279 | 1.0282 | 1.0285 | 1.0292 | 1.0324 | 1.0358 | 1.0396 | 1.0438 | 1.056 | 1.0719 | 1.2276 | 1.6449 | 1.4675 | 1.3694
CP/CV |  |  | 1.0263 | 1.0265 | 1.0268 | 1.027 | 1.0272 | 1.0274 | 1.0277 | 1.0279 | 1.0281 | 1.0286 | 1.0311 | 1.0339 | 1.037 | 1.0404 | 1.0507 | 1.0644 | 1.2063 | 1.5893 | 1.403 | 1.3024
CS |  | m/s | 113.0087 | 112.8571 | 112.6886 | 112.5198 | 112.3508 | 112.1816 | 112.0122 | 111.8425 | 111.6726 | 111.3322 | 109.6164 | 107.8772 | 106.1135 | 104.3245 | 99.7348 | 94.9671 | 74.4146 | 70.8654 | 97.1355 | 118.6678

## P vs H Diagram
Pressure vs Enthalpy Diagram for 3MTM NovecTM 1230 Fire Protection Fluid
Click on icon to open a pdf file of the Pressure vs. Enthalpy diagram

## Flooding Table SI
W/V table for 3M Novec 1230 fluid (FK-5-1-12mmy2)
| k1= | 0.0664 | k2= | 0.0002743
Total Flooding Quantity (SI Units)
Temp. | Specific | Weight Requirements of Hazard Volume, W/V (kg/m3)a
t | Vapor
(°C)b | Volume | Design Concentration (% by volume)d
| s | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
(m3/kg)c
-20 | 0.060914 | 0.50773 | 0.68402 | 0.86403 | 1.0479 | 1.2357 | 1.4275 | 1.6236 | 1.8241
-15 | 0.062286 | 0.49655 | 0.66896 | 0.84501 | 1.0248 | 1.2084 | 1.3961 | 1.5879 | 1.7839
-10 | 0.063657 | 0.48585 | 0.65455 | 0.8268 | 1.0027 | 1.1824 | 1.366 | 1.5537 | 1.7455
-5 | 0.065029 | 0.4756 | 0.64074 | 0.80936 | 0.98157 | 1.1575 | 1.3372 | 1.5209 | 1.7087
0 | 0.0664 | 0.46578 | 0.62751 | 0.79264 | 0.96129 | 1.1336 | 1.3096 | 1.4895 | 1.6734
5 | 0.067771 | 0.45635 | 0.61481 | 0.7766 | 0.94184 | 1.1106 | 1.2831 | 1.4593 | 1.6395
10 | 0.069143 | 0.4473 | 0.60262 | 0.7612 | 0.92316 | 1.0886 | 1.2576 | 1.4304 | 1.607
15 | 0.070515 | 0.4386 | 0.5909 | 0.74639 | 0.9052 | 1.0674 | 1.2332 | 1.4026 | 1.5757
20 | 0.071886 | 0.43023 | 0.57962 | 0.73215 | 0.88793 | 1.0471 | 1.2096 | 1.3758 | 1.5457
25 | 0.073258 | 0.42218 | 0.56877 | 0.71845 | 0.87131 | 1.0275 | 1.187 | 1.35 | 1.5167
30 | 0.074629 | 0.41442 | 0.55832 | 0.70524 | 0.85529 | 1.0086 | 1.1652 | 1.3252 | 1.4888
35 | 0.076 | 0.40694 | 0.54824 | 0.69252 | 0.83986 | 0.99037 | 1.1442 | 1.3013 | 1.462
40 | 0.077372 | 0.39973 | 0.53852 | 0.68024 | 0.82497 | 0.97282 | 1.1239 | 1.2783 | 1.4361
45 | 0.078743 | 0.39277 | 0.52914 | 0.66839 | 0.8106 | 0.95587 | 1.1043 | 1.256 | 1.4111
50 | 0.080115 | 0.38604 | 0.52009 | 0.65695 | 0.79673 | 0.93951 | 1.0854 | 1.2345 | 1.3869
55 | 0.081487 | 0.37955 | 0.51133 | 0.64589 | 0.78332 | 0.9237 | 1.0671 | 1.2137 | 1.3636
60 | 0.082858 | 0.37326 | 0.50287 | 0.6352 | 0.77035 | 0.90841 | 1.0495 | 1.1936 | 1.341
65 | 0.084229 | 0.36719 | 0.49468 | 0.62486 | 0.75781 | 0.89362 | 1.0324 | 1.1742 | 1.3191
70 | 0.085601 | 0.3613 | 0.48675 | 0.61485 | 0.74567 | 0.8793 | 1.0158 | 1.1554 | 1.298
75 | 0.086973 | 0.3556 | 0.47908 | 0.60515 | 0.73391 | 0.86543 | 0.99982 | 1.1372 | 1.2775
80 | 0.088344 | 0.35008 | 0.47164 | 0.59576 | 0.72251 | 0.852 | 0.98429 | 1.1195 | 1.2577
85 | 0.089716 | 0.34473 | 0.46443 | 0.58665 | 0.71147 | 0.83897 | 0.96925 | 1.1024 | 1.2385
90 | 0.091087 | 0.33954 | 0.45744 | 0.57782 | 0.70076 | 0.82634 | 0.95465 | 1.0858 | 1.2198
95 | 0.092458 | 0.33451 | 0.45065 | 0.56925 | 0.69036 | 0.81408 | 0.94049 | 1.0697 | 1.2017
100 | 0.09383 | 0.32962 | 0.44407 | 0.56092 | 0.68027 | 0.80218 | 0.92675 | 1.054 | 1.1842
a | W/V [Agent Weight Requirements (kg/m3)]= Kilograms of agent required per cubic meter of protected volume to produce indicated concentration at temperature specified.
|  |  | w = | V | C
|  |  |  | S | 100 - C
b | T [Temperature (°C)] - The design temperature in the hazard area.
c | s [specific volume (m3/kg)] of 3M Novec 1230 vapor can be approximated by the formula:
|  | s = 0.0664+0.000274T |  |  | where T is the temperature in °C
d | C [Concentration (%)] - Volumetric concentration of 3M Novec 1230 in air at the
temperature indicated.

## Flooding Table English
W/V table for 3M Novec 1230 fluid (FK-5-1-12mmy2)
| k1= | 0.9856 | k2= | 0.002441
Total Flooding Quantity (English Units)
Temp. | Specific | Weight Requirements of Hazard Volume, W/V (lb/ft3)a
t | Vapor
(°F)b | Volume | Design Concentration (% by volume)d
| s | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
(ft3/lb)c
-20 | 0.93678 | 0.033015 | 0.044479 | 0.056183 | 0.068137 | 0.080348 | 0.092825 | 0.10558 | 0.11861
-10 | 0.96119 | 0.032177 | 0.043349 | 0.054757 | 0.066407 | 0.078308 | 0.090468 | 0.10289 | 0.1156
0 | 0.9856 | 0.03138 | 0.042275 | 0.053401 | 0.064762 | 0.076369 | 0.088227 | 0.10035 | 0.11273
10 | 1.01 | 0.030621 | 0.041254 | 0.05211 | 0.063197 | 0.074523 | 0.086095 | 0.097921 | 0.11001
20 | 1.0344 | 0.029899 | 0.04028 | 0.05088 | 0.061706 | 0.072764 | 0.084063 | 0.09561 | 0.10741
30 | 1.0588 | 0.029209 | 0.039352 | 0.049707 | 0.060283 | 0.071087 | 0.082125 | 0.093406 | 0.10494
40 | 1.0832 | 0.028551 | 0.038465 | 0.048587 | 0.058925 | 0.069485 | 0.080274 | 0.091301 | 0.10257
50 | 1.1077 | 0.027922 | 0.037617 | 0.047516 | 0.057626 | 0.067954 | 0.078505 | 0.089289 | 0.10031
60 | 1.1321 | 0.02732 | 0.036806 | 0.046492 | 0.056384 | 0.066488 | 0.076813 | 0.087364 | 0.098149
70 | 1.1565 | 0.026743 | 0.036029 | 0.045511 | 0.055194 | 0.065085 | 0.075191 | 0.08552 | 0.096078
80 | 1.1809 | 0.02619 | 0.035284 | 0.04457 | 0.054053 | 0.06374 | 0.073637 | 0.083752 | 0.094092
90 | 1.2053 | 0.02566 | 0.03457 | 0.043667 | 0.052958 | 0.062449 | 0.072146 | 0.082056 | 0.092186
100 | 1.2297 | 0.025151 | 0.033884 | 0.0428 | 0.051907 | 0.061209 | 0.070714 | 0.080427 | 0.090356
110 | 1.2541 | 0.024661 | 0.033224 | 0.041967 | 0.050896 | 0.060018 | 0.069337 | 0.078862 | 0.088598
120 | 1.2785 | 0.02419 | 0.03259 | 0.041166 | 0.049925 | 0.058872 | 0.068013 | 0.077356 | 0.086906
130 | 1.3029 | 0.023737 | 0.031979 | 0.040395 | 0.048989 | 0.057769 | 0.066739 | 0.075907 | 0.085278
140 | 1.3273 | 0.023301 | 0.031391 | 0.039652 | 0.048088 | 0.056707 | 0.065512 | 0.074511 | 0.08371
150 | 1.3518 | 0.02288 | 0.030824 | 0.038936 | 0.04722 | 0.055682 | 0.064329 | 0.073165 | 0.082198
160 | 1.3762 | 0.022474 | 0.030277 | 0.038245 | 0.046383 | 0.054695 | 0.063188 | 0.071867 | 0.08074
170 | 1.4006 | 0.022082 | 0.02975 | 0.037579 | 0.045574 | 0.053742 | 0.062087 | 0.070615 | 0.079333
180 | 1.425 | 0.021704 | 0.02924 | 0.036935 | 0.044793 | 0.052821 | 0.061023 | 0.069405 | 0.077974
190 | 1.4494 | 0.021339 | 0.028748 | 0.036313 | 0.044039 | 0.051931 | 0.059995 | 0.068236 | 0.076661
200 | 1.4738 | 0.020985 | 0.028272 | 0.035711 | 0.04331 | 0.051071 | 0.059002 | 0.067106 | 0.075391
210 | 1.4982 | 0.020643 | 0.027811 | 0.03513 | 0.042604 | 0.050239 | 0.05804 | 0.066013 | 0.074163
220 | 1.5226 | 0.020312 | 0.027365 | 0.034566 | 0.041921 | 0.049434 | 0.05711 | 0.064955 | 0.072974
a | W/V [Agent Weight Requirements (lb/ft3)]= pounds of agent required per cubic feet of protected volume to produce indicated concentration at temperature specified.
|  |  | w = | V | C
|  |  |  | S | 100 - C
b | T [Temperature (°F)] - The design temperature in the hazard area.
c | s [specific volume (ft3/lb)] of 3M Novec 1230 vapor can be approximated by the formula:
|  | s = 0.9856+0.002441T |  |  | where T is the temperature in °F
d | C [Concentration (%)] - Volumetric concentration of 3M Novec 1230 in air at the
temperature indicated.

## s equations
s equations for Novec 1230 fluid
T (C) | T(F) | v (m^3/kg) | v (ft^3/lb)
-20 | -4 | 0.060668 | 0.97182
-15 | 5 | 0.062096 | 0.9947
-10 | 14 | 0.063518 | 1.0175
-5 | 23 | 0.064935 | 1.0402
0 | 32 | 0.066346 | 1.0628
5 | 41 | 0.067752 | 1.0853
10 | 50 | 0.069154 | 1.1078
15 | 59 | 0.070552 | 1.1301
20 | 68 | 0.071945 | 1.1525
25 | 77 | 0.073335 | 1.1747
30 | 86 | 0.074721 | 1.1969
35 | 95 | 0.076104 | 1.2191
40 | 104 | 0.077484 | 1.2412
45 | 113 | 0.078861 | 1.2632
50 | 122 | 0.080235 | 1.2853
55 | 131 | 0.081606 | 1.3072
60 | 140 | 0.082976 | 1.3292
65 | 149 | 0.084342 | 1.351
70 | 158 | 0.085707 | 1.3729
75 | 167 | 0.087069 | 1.3947
80 | 176 | 0.08843 | 1.4165
85 | 185 | 0.089788 | 1.4383
90 | 194 | 0.091145 | 1.46
95 | 203 | 0.0925 | 1.4817
100 | 212 | 0.093854 | 1.5034
105 | 221 | 0.095205 | 1.5251
110 | 230 | 0.096556 | 1.5467
115 | 239 | 0.097904 | 1.5683
120 | 248 | 0.099252 | 1.5899
125 | 257 | 0.1006 | 1.6114
130 | 266 | 0.10194 | 1.633
135 | 275 | 0.10329 | 1.6545
140 | 284 | 0.10463 | 1.676